## Slide 1: Paul Scherrer Institut
22. Oktober 2013
PSI,
Heat Recycling at PSI, a Project to Cover up to 75% of the Campus`s Heat Consumption
Reinhard David

## Slide 2: Introduction
Target of the presentation
Presentation of the boundary conditions and interfaces relevant to the realisation of the project
Facts an figures
Project scope and impressions
Agenda
General
PSI maps, sections and accelerators
Main power consumers
Potentials for efficiency improvements
Heat Recycling
Heating and building infrastructure
Cooling infrastructure, available heat sinks
Potential heat sources for heat recycling
A long term 2-step strategic plan for the heating system of PSI (Measures, Economy, Impressions)
Potential adsorption cooling

## Slide 3: PSI Overview
Number of Employees | 1500
Annual external user | 5000
Annual budget | 365Mio CH Fr
Annual cost of electricity | 3.5-4 % appr.
Annual cost of heat | 2‰ appr.
PSI’s scientific activities are strongly linked with the design, construction and operation of large and complex research facilities

## Slide 4: PSI Large Scale Research Facilities
22. Oktober 2013
PSI,
Swiss FEL
Proton Accelerator
(Myons, Neutrones)
Proscan (Proton Therapy)
Synchrotron Light Source: SLS

## Slide 5: Power Consumers PSI
SwissFel
6MW
Main electrical consumers (85%)

## Slide 6: Load Profile Power and Heat

## Slide 7: Saving Potential for Accelerators?
Example PSI-HIPA:
10MW total power  1,3MW proton beam power
RF: 4,1MW | 32% efficiency = already quite good, improvements difficult, potential low high cost
Magnets: 2,6MW | improvements possible, but high investments (new magnets)  not balanced by savings
aux.systems: 3,3MW | improvements possible and undertaken; often high investments
finally: 10MW heat | Heat recovery is investigated and used; Efficient use for smaller portion of high temperature RF cooling loop only.
thus important to utilize energy efficient technologies right from the design phase of an accelerator; later improvements are typically expensive and will not amortize
Heat Recycling is an important measure to decrease the use of primary energy

## Slide 8: Saving Potential of New Machines (Swiss FEL)?
  Swiss FEL is optimised for low energy consumption!
  compared with SACLA (Japan) reduced by -40%
  compared with LCLS (Stanford USA) reduced by -55%
  (statements from SwissFEL project management, background not subject of presentation)

## Slide 9: Saving Potential of New Machines (Swiss FEL)?
  Infrastructure
    Cooling Design (ground water, minimized through cascading temperature levels)
    HVAC concept and design (ventilation efficiency, very limited compression chillers)
    Class A components (Motors, Pumps, Ventilators, Filters, etc.)
    Heat Recycling (focus of this presentation)

## Slide 10: Heat Recycling Project
Relevant boundary conditions and criteria's
Building and heating infrastructure
Cooling infrastructure, available heat sinks
Potential heat sources for heat recycling
A long term 2-step strategic plan for the heating system of PSI (Measures, Economy, Impressions)
Potential adsorption cooling

## Slide 11: Building Infrastructure of PSI Campus
Building Infrastructure and condition, casing and insulation
Age from 0 to 50 years
Office, laboratories and functional buildings with high internal heat loads
Some huts as permanent interim arrangements
Closed but still legal «research atomic reactor buildings»
Buildings to be removed but ever and ever used
Reduction of heat consumption by passive insulation less effective than waste heat recycling but very costly!

## Slide 12: Heating Infrastructure of PSI Campus
District heating system Refuna
Heat source nuclear power plant Beznau I+II
Future heat source unknown, today`s low CO2-emission source not further guaranteed!
System designed for high temperature of 115°C

## Slide 13: Todays and Future Heat Consumption and Costs
Actual consumption = expected long term consumption=12GWh
  Yearly cost: 750kFr
  Future cost: ??? (actual heat price is based on process heat from nuclear power plant Beznau), price increase very likely!

## Slide 14: Heat Sinks PSI
River “Aare” 15MW (cavities, magnets, …)
Ground water 5MW (+6MW from 2017 for SwissFEL) (various, 3 cascading circuits )
Air 2.5MW +5MW (direct+indirect mainly for HVAC`s only)
Total 27.5 MW (33.5 MW incl. SwissFEL)
Rich Groundwater @12°C…14°C
River Aare @ 1…24°C
→Most efficient cooling systems with very little compressing cooling machines in terms of energy! (capacity is 5MW for peak and/or summer loads or redundancy)

## Slide 15: Potential Heat Sources and Demand
Category 1: 4MW @ appr. 60°C
Category 2: 18MW @ appr. 30°C

## Slide 16: 2 Step Strategy - Step 1
Direct use of waste heat category 1 (>60°C)
Increase use of waste heat from 20% to 75% appr.
Required Measures
Separation of heating water cycle (Refuna / PSI)
Integration of heat sources category 1
Temperature decrase:
    Modification of building heating stations
    Replacement of Radiators
    Replacement of ventilation heaters
Projekt in Execution now!

## Slide 17: Integration of Heat Sources
Integration of 4 existing sources and separation of PSI heating cycle: 700kFr

## Slide 18: Replacement of Radiators
1500 Radiators have to be replaced
Costs: 1500kFr
Original Design: 70/50°C
New Design: 45/30°C

## Slide 19: Heat Exchangers of Building Heating Stations
Existing heat exchanger with dTm=22K
(type pipe bundle)
37 heat transfer stations to be adapted: 700kFr
Existing heat exchanger with dTm=5K
(plate type fusion bonded, stainless steel)
→very compact

## Slide 20: Ventillation Heaters
Original Design Temperature 50…80°C → New Design Temperature 35/20°C
150 heat exchangers to be replaced: 700kFr

## Slide 21: New District Heat Pipe for Waste Heat Swiss FEL
1000m of ground pipe
Costs: 600kFr
(ditch was needed for other puprose as well)

## Slide 22: Temperature Decrease to Comply with Heat Sources

## Slide 23: Project Heat Recovery Step 2 (Future Option)
    Direct use of heat sources category 1
    Indirect use of heat sources category 2 via heat pumps (Increase 20K)
    oil for peakload /backup)
    Required Measures:
      All measures step 1
      Installation of heat pumps of 3MW approximately
Future Option!

## Slide 24: Project Heat Recovery Step 2 (Future Option)

## Slide 25: Economy Heatrecovery Step 2
Measures, Costs, timescale, economy, pictures
→ We have an alternative to todays efficient district heating system
comparable economy

## Slide 26: Potential for Adsorption Cooling
Angebot und Nachfrage von Kälte und Wärme
0
1000
2000
3000
4000
5000
6000
0
1000
2000
3000
4000
5000
6000
7000
8000
Jahresstunden
Leistung in KW
Durchschnittlicher Kältebedarf
PSI
Heizwärmebedarf PSI
Bandlast Abwärme SwissFEL
1'800kW
Wärmebedarf für Kälte
Wärmebedarf total
Heat excess
Cold water produced with heat: 2200 MWh

## Slide 27: Potential for Adsorption Cooling
Demand matches availability of cooling circuit for 5 laboratories
Feasibility is given but temperature level is at limit and to find space for installation (recooling!) is a challenge
Estimated costs with 1.8Mio above maximal economical investment of 1.3Mio.

## Slide 28: Conclusions
For the PSI it is effective and economic to recycle waste heat
A considerable investment of 4Mio approximately was permitted
Heat recycling is more effective and much more cost efficient than reducing the heat consumption by passive insulation only.
Optimised campus wide energy concepts with a long-term stategy are highly recommended since according our experience more effective than fulfilling typical energy standards for buildings only!
The Project supports
Reduction of Primary Energy
Reduction of Cost for Energy

## Slide 29
22. Oktober 2013
PSI,
Thank you for jour attention!

## Slide 30: Jahresarbeitszahl Refuna
    COP= Coefficient of Performance (Leistungsziffer),
    COP =Qheiz/Pel, Coefficient of Performance bedeutet, dass beim Bezug von 6.5MW thermisch 1 MW El. Leistung eingesetzt werden muss. Physikalisch: 1/eta,carnot, wobei eta,carnot an 2-ten Hauptsatz der Thermodynamik gebunden ist: eta,carnot =(Tzu-Tab)/Tzu.
    COP der Refuna: 6.5 Netto *)
Strom
-1MW
Wärme
+6.5MW
Verrifikation auf theor. Basis *)