## Slide 1: HV insulation tests for WP3 busbars
A. Milanese, L. Grand-Clement
Acknowledgment: H. Prin, R. Principe, D. Tommasini
14 Apr. 2021

## Slide 2: Introduction
HV tests to qualify the dielectric robustness of individual components (busbars in this case) before they become part of a system (cold mass or superconducting circuit in the tunnel)
  Test voltage of component > final test voltage of system
  Aim to intercept a faulty construction
  Even more relevant considering
    difficulty of repair in case of electric fault during operation
    relative cost of busbars vs. final system
  Same philosophy being applied to new generation of MQXFB QHs
    few units already successfully tested at 10 kV

## Slide 3: Cela est rare, mais cela arrive…

## Slide 4: Scope of proposed HV tests
Several test objects
    internal busbars MQXF
    N1 line busbars MQXF, N2 line busbars MCBXF
    busbars MCBRD
    DCM/DFX busbars, DFM busbars
  Three types of (routine) tests
    before insertion in cold mass (or N lines or L plates)
    after insertion in cold mass, before connection to magnets
    after connection to magnets --- not covered here, as already part of other electrical test documents [though increased voltages across different circuits shall be added]
  Tests at room temperature for virgin components
    in air at atmospheric pressure
  Type (as opposed to routine) tests could be relevant too
    ex. breakdown in He gas on samples of internal MQXF busbars

## Slide 5: Internal busbars MQXF (18 kA)
Busbars provided by AUP
  NbTi cable provided by CERN
E. Todesco
EDMS 2029211 v.0.7

## Slide 6: Internal busbars MQXF (18 kA)
local bus and through bus
chassis = set of each metallic screw closing the housing + aluminium supports
FNAL drawings
EDMS 2515485

## Slide 7: Internal busbars MQXF (18 kA)
Two units already delivered by AUP

## Slide 8: From the FNAL LMQXFB Bus Bar Traveler

## Slide 9: Internal busbars MQXF (18 kA)
  As received, before insertion into cold mass
    5 kV bars to chassis
      slightly higher than current (3.68 kV) used in FNAL for the housing, plus the chassis includes the housing clips and also the metallic screws
    5 kV local bus to through bus, chassis grounded
  After insertion into cold mass, after shaping the extremities but before connection to the leads
    5 kV bars to cold mass (yoke and coils) grounded
    5 kV local bus to through bus, cold mass (yoke and coils) grounded
E. Todesco
EDMS 2029211 v.0.7

## Slide 10: N1 line busbars MQXF (18 kA)
E. Todesco
EDMS 2029211 v.0.7
Round cable being procured by TE-MSC-SCD
Insulation (2×3×50 mm of polyimide) and (non conductive) mechanical reinforcement
  see presentation of J. Fleiter
Bundle of two for mains, single cables for trims
Non conductive sleeve put in place around the cables, but no support to hold them in N lines
  see presentations of J. Fleiter and H. Prin

## Slide 11: N1 line busbars MQXF (18 kA)
E. Todesco
EDMS 2029211 v.0.7
  As received, before insertion into N lines
    5 kV cable to cable for the bundle of two
    5 kV cable(s) to external surface
      external surface = bath of metallic balls (similar principle for LHC busbars) or Al foil (wrapped around the delivered cable)
    insulation to be tested continuously online at 10 kV at cable production, see presentation of J. Fleiter
  After insertion into N lines, before splicing
    cables already bent
    5 kV each cable to N line tube + all other cables grounded

## Slide 12: N2 line busbars MCBXF (2 kA)
E. Todesco
EDMS 2029211 v.0.7

## Slide 13: N2 line busbars MCBXF (2 kA)
Round cable being procured by TE-MSC-SCD
Insulation (2×3×50 mm of polyimide) and (non conductive) mechanical reinforcement
  see presentation of J. Fleiter
Bundle of two × two for mains of vertical / horizontal corrector
  As received, before insertion into N lines
    5 kV each cable to all other cables (bundle of four)
    5 kV cables to external surface
      external surface = bath of metallic balls or Al foil (wrapped around the delivered cable)
    insulation to be tested continuously online at 10 kV at cable production, see presentation of J. Fleiter
  After insertion into N lines, before splicing
    5 kV each cable to N line tube + all other cables grounded

## Slide 14: Internal / N line busbars MCBRD (600 A)
E. Todesco
EDMS 2029211 v.0.7
  Bundles of 2 × 2 cables, provided by TE-MSC-SCD
    same as used in LHC (orbit correctors, trim quads, etc.)
    in a stainless steel sheath
    internal part: in a goulotte
    external part: protected in a PP pliozip and then inserted in a N line like tube

## Slide 15: Internal / N line busbars MCBRD (600 A)
E. Todesco
EDMS 2029211 v.0.7
  As received, before insertion into cold mass
    5 kV each cable to external metallic sheath + all other cables (bundle of four) grounded
    single cable recently tested at 10 kV
  After insertion into cold mass, before splicing
    5 kV each cable to cold mass (yoke and coils) + all other cables grounded

## Slide 16: DCM/DFX busbars
E. Todesco
EDMS 2029211 v.0.7
  only one case for MCBXF shown

## Slide 17: DCM/DFX busbars and DFM busbars
Same round cable as for N lines
7 × 18 kA
    5 for MQXFB (2 main + 3 trims)
    2 for MBXF
  3 × 4 × 2 kA
    bundle of 4 for each MCBXF
  As received, before preparation of the plugs
    as before, this is a test of the individual cable or bundle of cables
  After insertion into L plate
    5 kV each cable (18 or 2 kA) to plate + all other cables grounded
      particularly relevant for bundles of 4
  Similar tests after welding of L plate in DCM
  Cold diodes to be discussed
topic more for DCM review
DFM case similar
(simpler, no diodes and less plugs)

## Slide 18: Other considerations and conclusion
Proper EDMS document to be prepared and approved
  ex. Flowchart of the electrical tests throughout the production of LQMXFB, 2447487
  consider type tests and production tests
  detail voltage ramp, test durations and max. leakage currents
  discuss possible dielectric resistance measurement at intermediate voltage before / after high voltage leakage current test
  repairs in case of certain faults can be a possibility
  acceptance test of various round cable to be discussed also according to design
Splices insulations
    not covered separately, designed and executed to withstand test voltages as the corresponding circuit
  Keep in mind in the design and inspections also LHC experience
    13 kA busbars a bit too close to ground and experiencing thermal movements
    recent reminders for MB and SSS 500…

## Slide 19: References
2029211
HL-LHC WP3 Bus Bars technical specification and conceptual lay out
1963398
HL-LHC Electrical Design Criteria for the IT magnets
2187266
HL-LHC Electrical Design Criteria for the D1 dipole
2363905
HL-LHC Electrical Design Criteria for the MCBXF dipole corrector
2363904
HL-LHC Electrical Design Criteria for the D2 dipole
2363906
HL-LHC Electrical Design Criteria for the MCBRD dipole corrector
90327
Voltage withstand levels for electrical insulation tests on components and bus bar cross sections for the different LHC machine circuits
1158606
Procédure de test de l'isolation des bus bars après enrubannage

## Slide 20: Are the test voltage levels appropriate?
5 kV 10 kV?
Ok in principle, though as a remainder LHC busbars were tested at 5 kV
Voltages across different circuits in close proximity (N lines) to be considered

## Slide 21
Thank you

## Slide 22: HL-LHC IT magnets

## Slide 23: HL-LHC D1 magnets

## Slide 24: HL-LHC D2 magnets

## Slide 25: HL-LHC MCBXF magnets

## Slide 26: HL-LHC MCBRD magnets