## Slide 1: Forward Physics Facility (FPF) Civil Engineering Study Update
Kincső Balázs, John Osborne SCE-DOD-FS
Date: 27/05/2021

## Slide 2: Introduction
Experimental Requirements and CE considerations
Option 1: Alcoves in the UJ 12
Option 2: Purpose built facility
Next Steps

## Slide 3: Experimental requirements and CE consideration
Requirements:
Experimental area approx. 500-600 m away from LHC P1 or P5 on the Line of sight (LoS)
Space for experiments
Access needed for construction, installation and maintenance
CE considerations:
Existing infrastructure
Access for construction
Disruption to LHC machine
Geology
Cost

## Slide 4: CE Study Update- Considered options
  Option 1 – UJ12 Alcoves
4
4
4
TI12
LHC
IP1 ATLAS
UJ12
PGC3 Shaft
SPS
  Option 2 – Purpose built facility

## Slide 5: Option 1 – Alcoves in UJ12
Advantages
  Lowest cost and disruption
Disadvantages
  Experiments need to be designed around what is possible
  Likely only 2-3 alcoves possible around 3mØ
  Stability of existing cavern
  All existing services in UJ12 need to be removed
5
Plan view showing widening and alcoves
Typical Alcove Cross Section C-C
3D view
Alcove Cross Section at B-B

## Slide 6: Option 1 – SPS Beam Dump tunnel eye enlargement as a reference
Easier access compared to UJ12
  Access via 3m PGC3 shaft and via TT12
Single enlargement
Part of the services kept during the CE works
PGC3 Shaft
Abandoned TI12 tunnel
SPS tunnel
ATLAS

## Slide 7: Option 1 – Very Preliminary Cost Estimate for CE works
Preliminary Cost Estimate
Methodology
Comparative Costing
SPS Dump Facility Tunnel eye enlargement as reference point
Cost Estimate Class 4 – total could be 50% higher and 30% lower than the given estimate
Assumptions
Removal of the existing services and equipment from the UJ12 not included
Services (CV, electricity etc.) not included
7
7
Draft

## Slide 8: Option 2 – Purpose built facility
Advantages
  Designed around needs of experiments
  Size/ length not constrained
  Construction access far easier
Disadvantages
  More expensive
  Construction still need to be coordinated with LHC shutdowns
8
existing
proposed

## Slide 9: Option 2 – Purpose built facility
Proposed Layout
65 m long Experimental Cavern located on the LoS, approx. 612 m from IP1
9.1 m access shaft located on the top of the cavern
Safety gallery connecting the cavern to the LHC to avoid dead-end
LHC tunnel
SPS tunnel
Line of sight (red)
FPF
Plan view

## Slide 10: Option 2 – Underground structures
9.7 m wide cavern to allow access for transport and siting of some services
Experiments centralised on the line of sight, 1.5m above the floor
Floor parallel to the LoS, 1.25%fall
Trench under the LAr detector to catch any escaped cold gas
Concept based on overhead crane serving experiments along cavern length

## Slide 11: Option 2 – Underground structures
88m deep shaft includes lift and stairs for access and space reserved for transport
Safety gallery connected to the LHC as per Safety requirements
Ongoing discussions with the HE and RP department
Section through the new cavern and the safety gallery
Cross section through the shaft
Plan view shaft

## Slide 12: Option 2 – Surface buildings
CV building
Electrical building
25t overhead crane
False floor
Access Building
Transformer base
Access building
Similar in size to SD1 and SD17
Steel portal frame structure with concrete ground bearing floor
2.5 m deep false floor surrounding the shaft
25t overhead crane to lower the experiments to the floor level of the cavern

## Slide 13: Option 2 – Surface buildings
Service Buildings
Electrical, cooling and ventilation building adjacent to the access building
Electrical building designed as a steel frame structure
Similar size to HL-LHC point 1
1.2m deep false floor to allow the services to be distributed into the shaft with a concrete access platform for vehicles to enter the buildings
Access building
Tank base
CV building
False floor
Vehicle access platform
Transformer base
Electrical building

## Slide 14: Option 2 – Costing Methodology
Methodology:
Comparative Costing
HL-LHC Point 1 as reference point
Cost Estimate Class 4 – total could be 50% higher and 30% lower than the given estimate
Assumptions:
Project Management included as % of the CE works
Services (CE, electricity etc.) and technical galleries not included
Environmental impact study not included
Landscaping and excavation volume to be further studied

## Slide 15: Option 2 – Very Preliminary Cost Estimate for CE
Draft
Chart: Split of the CE cost
| Common Items | Underground Works | Surface Buildings | Miscellaneous
 | 0.27339 | 0.38103 | 0.28379 | 0.061787
Chart: Split of underground work
| Access shaft | Experimental cavern | Safety gallery
 | 0.52113 | 0.42046 | 0.058414

## Slide 16: Option 2- Preliminary Schedule
Note: Pre-construction activities not included in the schedule

## Slide 17: Next Steps
Develop concept design further with detailed input from Integration, Transport, CV, Cryogenic, Radiation Protection and Heath and Safety teams
Decide on the option to further develop
Progress with cost estimate and schedule

## Slide 18
Thank you!