## Slide 1: East Area Renovation – Cabling campaign 11th EN-EA East Area Equipment Review 04.06.2021
A. ALONSO (BE-EA)

## Slide 2: Cabling campaign
Control cables
Old control cables removal
DC cables
Old DC cables removal
Earthing
Worker installing connectors

## Slide 3: Phases of the Project
PHASE 1
PHASE 2
PHASE 3
PHASE 4
PHASE 5
PHASE 6
PHASE 7
Various
04/06/2021

## Slide 4: Control cabling
652 Cables on the original planning
  30 Removed
  244 Modified
  21 Modified twice
860 Connectors
728 Cables at the moment
50,5 Km of cables
96% Completion
More cables are expected to be added during construction, commisioning or even operation
Cable bridge created to pass cables to the exterior of the building

## Slide 5: Old control cable removal
4,5 Km of cables removed
Cables to be removed at exterior of the building
A few cables remaining
Pink label mark a cable to be removed

## Slide 6: DC cabling
128 DC cables
  36 cables of 120 mm2
  92 cables of 240 mm2
Joining the old cables with the new ones at the gallery
The external surface in some remaining cables is not in perfect conditions.
Possible manipulation or movement could cause damage of insulation
Example of cable rusted and burned in the gallery
Last 2 magnets to be installed
Old situation
New situation
40 m

## Slide 7: Old DC cable removal
120 cables removed
7,2 Km of cables
Old DC cables to be kept at Building 251
Old DC cables to be removed at the gallery
3 more weeks of work remaining
The extracted cables will be sold and the money will cover the extraction job and more
Removed cables waiting to be sold to recycle

## Slide 8: Earthing
Around 100 elements to be grounded
80% Completed
20% Elements not at place yet
CERN orders a minimum of 16 mm2 of earthing
For the equipment connected to DC cables 35 mm2 and 50 mm2 of earthing cable were used for extra safety
20% equipment missing

## Slide 9: Thanks for your attention !
04/06/2021