## Slide 1: New Cable Rule “SSI-FS-2-1” Replacing IS 23
A. Henriques – HSE/OHS
31 March 2022
EXSO Meeting

## Slide 2: New rule on cables
Objectives:
Replace (outdated) CERN specific standard where possible by state-of-the-art classification in EU  Construction Products Regulation (CPR)
Improve safety and quality of cables  CPR class Cca (mandatory class for underground in F/CH, includes quality assurance)
Facilitate the purchasing of cables  CPR: industry compatible standard
Allow flexibility in the requirements for non-standards cables – e.g. microduct FO cables, signal cables, etc. or in-kind contributions  “Performance-based approach” / equivalent safety level
Improve radiation resistance requirements, based on lessons learnt

## Slide 3: Purpose & Scope
Scope:
Future cables brought on the CERN site.
Requirements linked to:
fire performance (reaction, resistance, halogen content, toxicity,...)
Radiation resistance
…of cables at CERN
added optical fibres
Excluded:
Cables in CE Marked equipment
  Incl. stand-alone short connection cords
Lifts (except LHC lifts)
Connection cords
Result of ~3 years of stakeholder discussions with organic units purchasing or specifying cables

## Slide 4: Fire Reaction
EU market:
  Risk-based typology approach for cables classes (EU member state approach)
Hostel/creche
Underground
Tertiary bldgs.
For example:
Temporary installations
Cca - s2, d1, a2
Acidity of smoke (i.e. halogen presence)
Smoke production (i.e eyesight during evacuation)
Droplets (i.e. fire propagation)
Fire reaction (i.e. heat generated)
Align with the EU approach (CPR ) – in force for cables since 2017

## Slide 5: Fire Reaction
Minimum CPR class
Cca - s2, d1, a2
‘High-risk’ installation:
Dca - s2, d1, a2
‘Low-risk’ installation:
Safety Guideline SG-FS-2-1-1
Case-by-case optimization
(e.g. technical incompatibility, certification other than CPR)
Risk Assessment
or
Common questions:
Final location of the cables is unknown. Which to choose ?
 Cca – s2, d1, a2
Trouble with finding suitable suppliers for in-house purchases ?
Market is still reacting to the CPR. More and more suppliers are performing the necessary tests little-by-little.
Technically incompatible – case-specific risk assessment
Why Cca class for High-risk inst.?
Regulatory level: in-line with Host States
Technical level: see spare slide
What about for in-kind contributions?

## Slide 6: Fire Reaction
Case-by-case Risk Assessment
In-kind contributions from non EEA countries
e.g. Large Experiments
Aim for equivalent performance level
(e.g. US test standards)
OK
Missing
Ok
Ok
Missing

## Slide 7: Fire Reaction
Case-by-case Risk Assessment
Technical limitations (special cases)
No CPR class –
LSZH class required
(necessary tests in the Guideline)
PTFE sleeves
in low temp.
application
PTFE RF
connectors
PTFE allowed in minimal quantities - no alternative available

## Slide 8: Fire Resistance
Cables that shall maintain their functionally in accidental situations (e.g. fire) for a specific amount of time
Cables powering ‘Safety Systems’ (e.g. emergency lights, fire doors, smoke extraction, etc.)
Higher or Lower performance may be acceptable:
Risk Assessment
PH 90
(integrity for 90min)
Default requirement:

## Slide 9: Radiation Resistance
IS 23:
Lifetime dose > 100 Gy:
  General purpose cables:
  RI 5.7  test at
Special radiation resistant cables
  RI 7.7  test at
Slight modification to IS23
SSI-FS-2-1:
Lifetime dose > 100 Gy:
  Multi-purpose application cables (CERN stores)
  RI 5.7  test at
Lifetime dose > 2 MGy:
  RI 7.0  test at
Case-specific RI class with expected lifetime dose:
  RI  test at
  Safety factor of 5 – see Guideline
Notes: Motivation: Retention of functional capabilities of the cable subject to radiation doses / avoid unjustified de-cabling campaigns
DED - dose to equivalent damage
Measured at an elongation endpoint criteria at 50%
DED 0.50
Sample tests Draka cables: SVA3 and SVA3R

## Slide 10: Conclusion
Improves safety and quality of cables
Facilitates the purchasing of cables: industrial vs CERN-specific standard
Procurement: impact mainly driven by the market (in force since 2017)
  Extra costs or procurement delays will decrease over time as market adapts
The “risk assessment approach” addresses the flexibility required for non-standards cables or coming from outside the EEA
Radiation resistant requirements improved based on lessons learnt and findings from projects looking at cable aging and deterioration under radiation environments.
Rule comes with a Safety Guideline with additional (technical) information to ease implementation
https://hse.cern/content/safety-rules
https://edms.cern.ch/ui/file/2669584/LAST_RELEASED/SSI-FS-2-1_EN.pdf
https://edms.cern.ch/ui/file/2669629/LAST_RELEASED/SG-FS-2-1-1_EN.pdf
Rule: SSI-FS-2-1
Guideline: SG-FS-2-1-1

## Slide 12: New EU regulation on fire reaction of cables
Construction Products Regulation (CPR), compulsory for cables in the EEA open market from June 2017
  IS23 vs CPR
Tests | IS23 | CPR
Fire Reaction/ Propagation | IEC 60332 (EN 60332) | EN 60332 + EN 50339
Smoke production | IEC 61034 (EN 61034) | EN 61034
Droplets | - | EN 50399
Smoke acidity | IEC 60754 (EN 60754) | EN 60754
Toxicity | IEC 60695 | Not by default, only ‘major Safety implications’
CPR = IS23 + EN 50399 tests
EC Decision 2006/751/EC:
EN 50399 provides additional requirements linked to fire reaction and droplets
Only
Low Smoke
Zero Halogen
EU Fire
Safety Strategy
(life safety)

## Slide 13: Proposal class Cca-s2,d1,a2
Technical
Class Cca over Dca
Factor 7x lower maximum (peak) heat release rate
Factor 4x slower fire growth rate
…
Subclasses s2,d1,a2
The minimum level where the impact is measurable
e.g. s2 = smoke production between 0.25 and 1.5 m2/s
s3 = smoke production greater than 1.5 m2/s….
Quality assurance
From Dca to Cca = Large gain in cable quality
Stakeholder discussions: the re-establishment of a Quality Assurance process for the procured cables at CERN is needed
Dca : ‘Self-certification’
Cca : Certification by notified body + samples tests
Dca not allowed in underground areas by most EU countries
Regulatory
Minimum subclasses required in evacuation routes: s2,d1,a2
Subclasses required in household, underground tunnels: s1,d1,a1

## Slide 14: Technical data Cca-s2,d1,a2
Class Cca v Dca
Subclasses s2, d1, a2
performance not measurable ( ‘greater than…’)
Dca not allowed in underground areas by most EU countries

## Slide 15: Quality Assurance class Cca
[1] RIACWG Final Report – EDMS N. 1369134
Cca v Dca

## Slide 16: EU members sub-classes: s2,d1,a2
Classes allowed in evacuation routes:
s2,d1,a2
Classes allowed by type of infrastructure:
  Household: s1,d1,a1 (Cca)
  Road tunnels: s1,d1,a1 (Cca)
  Railway tunnels: s1a,d1,a1 (B2ca)
Lower performance than e.g. FR/GE is acceptable due to the occupancy rate in CERN installations w.r.t. road/railway tunnels, apartment blocks, etc.
Classes allowed by type of infrastructure:
  Evacuation routes: s1,d1,a1
  Underground: s1,d2,a1
  (non egress)
Notes: 183 total euroclasses
Zero Halogen means HCI (hydrogen chloride) < 0.5 % of combustion gases -> HCL when mixed with water forms Hydrochloric acid which swells the throat

## Slide 17: Fire reaction tests Cca vs Dca

## Slide 18: CRP class in Switzerland (egress)
s2,d1,a2
Minimum allowed for egress
Notes: 183 total euroclasses
Zero Halogen means HCI (hydrogen chloride) < 0.5 % of combustion gases -> HCL when mixed with water forms Hydrochloric acid which swells the throat

## Slide 19
CRP class in France

## Slide 20: Radiation Resistance – Material table
Classification of materials according to their radiation resistance
[Ref] Compilation of radiation damage test data, part 1 2nd edition.: Halogen-free cable-insulating materials; H. Schönbacher, M. Tavlet;
CERN 89-12 Yellow Book
XLPE
EPR
Mentioned in cable spec*:
Template for Technical Specifications - Supply of Cables – EDMS N. 1137965
RIACWG Final Report – EDMS N. 1369134
*
Megolon®