## Slide 1: Diagnostics and Prognostics for Power Electronics Converters in Large-scale Accelerator Facilities
NorCC: Student Seminar 01.02.2022
Timm Felix Baumann
Norwegian University of Science and Technology

## Slide 2: Content
Self introduction CV
PhD timeline and supervision
Converters for accelerator
Research field condition monitoring
Current work
Discussion

## Slide 3: Timm Felix Baumann
Master in Electrical Engineering
Master of Education in Electrical Engineering
Bachelor in Electrical Engineering
Apprenticeship Electronic Technician
Openstreetmap.org
Thun Switzerland

## Slide 4: Timeline PhD Project
Collaboration between NTNU and CERN
1 year NTNU (Mai 2021 – April 2022)
1.5 years CERN (Mai 2022 – October 2023)
0.5 – 1 years NTNU (November 2023)

## Slide 5: Supervision
NTNU
Dimosthenis Peftitsis
Ole-Morten Midtgård
CERN
Konstantinos Papastergiou
Raul Murillo Garcia

## Slide 6: Converter for accelerator
Load: Magnets to focus the particle beam
Single phase high inductive load
High precision current pulse required
Energy storage to enable recovery and minimise grid load

## Slide 7: Example output pulse of converter
I
t

## Slide 8: Example SIRIUS converter

## Slide 9: Example SIRIUS converter
Capacitor bank 900V down to 450V during cycle!
400V
300V
450 .. 900V
-450 .. +450V

## Slide 10: Converter for accelerator
Not standard requirements (cost, size, reliability)  Accuracy and reliability most relevant
Highly integrated in Network
Components are oversized for better reliability
  Good for CERN but even harder to detect degradation

## Slide 12: Critical components
Capacitors (electrolytic capacitors)
Semiconductors
Auxiliary (drivers, cooling, …)

## Slide 13: Diagnostics and prognosis
Still implemented at CERN: Interlock system / alarms
  Digital signals: overtemperature, door contacts, overvoltage, …
  Indicates failures and failure points  safety and failure search
New for CERN: condition monitoring (CM) system
  Nonbinary information: e.g. temperature actual 95°C (normal 90°C, maximal 110°C)
  State of health (SOH) approximation
  How will SOH change in future  prognosis

## Slide 14: Data acquisition methods for CM
«online measurement»
«offline measurement»
«quasi offline measurement»
Modelling without measurements
converter
converter
converter
measure
measure
measure
load profile
SOH calc
SOH calc
SOH calc
SOH calc

## Slide 15: Data acquisition methods for CM
Each additional circuit can fail and moreover can reduce the reliability of the entire system!
Using same system as for control is used
Load profile based simulations (no measurements)
System design to enable CM

## Slide 16: Data analysis deterministic vs AI
Deterministic is best  fully understand behaviour 😊
AI output quality depends on training data quality and quantity
  Critical point for power electronics
Combinations are possible
  Deterministic parameter calculation as input for AI
  AI used to predict a parameter which is used in a deterministic model

## Slide 17: Capacitor diagnostics project
Ageing effect of capacitor bank is expected decreasing capacity and increasing leakage current
Condition monitoring for the capacitor bank by doing dischargeing curve analyses
Timeconstant R*C calculation  SOH
Use of existing voltage sensor and communication
Use of the turn-off phase of the convertors

## Slide 18: SIRIUS converter capacitor analysis
All switches are off
Discharge over balancing and discharging resistors
900 .. 0V

## Slide 19: Capacitor bank

## Slide 20: Recorded data

## Slide 21: Optimised sampling
Publication planned for

## Slide 22: Laboratory MOSFET cycling build up
Verification of ageing mechanisms
Production of aged samples
Reactivate existing build up
Neu build up for parallel cycling

## Slide 23: Idea thermal monitoring
Static behaviour (constant power dissipation)
  PD as indicator itself
  Thermal leakage (PD, power in cooling water) e.g. solder layer degradation
  Quality / SOH of water cooling system (T heatsink, in, out, flow rate)
Dynamic behaviour / delay of thermal flow
  Reconstruction of thermal network
Chip
(Thermal resistance)
T_in
T_out
T_heatsink
T_ambient
Power dissipation (PD)
Water cooling system
T_box
Flow rate
(T_junction)

## Slide 24: Transient example normal operation
PD
t
T_junction
t
T_heatsink
t
T_water_out
t

## Slide 25: Transient example ageing effects
PD
t
T_junction
t
T_heatsink
t
T_water_out
t
Faster heat up
Higher temp
Slower cool down
Increased PD
Increasing thermal resistance
Slower heat up
lower temp due leakage
Cool down both possible

## Slide 26: Questions
«risk» of low / hard detectable degradation
Thermal monitoring
Further approaches

## Slide 27: Discussion round