## Slide 1: Overview PSI RF Systems power consumption
M. Pedrozzi :: In behalf of the PSI RF group :: Paul Scherrer Institute
Workshop on efficient RF sources - July 4-6 2022

## Slide 2: PSI's accelerators in the landscape
Page 2
HIPA ~52’000 MWh/year
  (High Intensity Proton Accelerator)
SLS ~16’000 MWh/year
  (Swiss Synchrotron Light Source)
SwissFEL ~22’500 MWh/year
  (Swiss X-Ray Free Electron Laser)
PROSCAN ~4’700 MWh/year
  (Proton therapy, not handled here)
1.
4.
3.
2.

## Slide 3: Overview High Intensity Proton Accelerator
Regular operation at 2.2mA beam current
1.29 MW beam power
Tested up to 2.4 mA beam current
1.4 MW beam power
n2EDM
1.
SμS: Swiss Muon Source
Injector 2
72 MeV
Proton source
Global Rf power requirement ~6 MW
(50% of overall requirements)
Notes: SINQ: neutron spallation source (SpallatIon-NeutronQuelle)
UCN: Ultra Cold neutrons
  (n2EDM: neutron electric dipole moment experiment)
Target M & E: Muon sources

## Slide 4: Injector 2 cyclotron
Injection energy: 870 keV
Extraction energy: 72 MeV
Number of turns: 83
Resonator | type | material | frequency | gap voltage | Wall losses in cavity | incident power @ 2.4 mA Beam
1 & 3 | Double gap cavity | aluminum | 50 MHz |  420 kVp |  150 kW |  225 kW
2 & 4 | Flattop cavity | aluminum | 150 MHz |  31 kVp |  5 kW |  14 kW
2 & 4 new | Single gap cavity | aluminum | 50 MHz |  400 kVp @ extraction |  50 kW |  100 kW
1.
Ongoing Upgrade
Replacement resonator 2&4
New Tetrode amplifier chain and LLRF all resonators
Goal: Increase voltage toward 3 mA beam current
No efficiency gain expected

## Slide 5: Ring cyclotron
numbers | type | material | frequency | gap voltage | incident power no beam | incident power @ 2.4 mA beam
4 | Main cavity | copper | 50 MHz |  850 kVp |  250 kW |  600 kW
1 | Flattop cavity | aluminum | 150 MHz | 555 kVp |  110 kW (active) |  - 36 kW (passive)
copper cavity
Sector magnet
Flattop cavity
Injection energy: 72 MeV
Extraction energy: 590 MeV
Number of turns: 186
1.

## Slide 6: Amplifier chain for one copper cavity in ring cyclotron
1kW 10kW 100kW 1MW
Amplifier chains built in early 90s
Some parts were taken over from older rf-system.
1.

## Slide 7: Amplifier chain for one copper cavity in ring cyclotron
100kW 1MW
2022: 1/10kW Tetrode Amplifier replaced by 10kW SSA (BBL200-A10000 from Rohde & Schwarz)
Of the shelf SSA operated in class A -> no improvement in efficiency, goal is reliability
1.

## Slide 8: Power efficiency rf systems for the Ring cyclotron
 | filament on | no Beam | 2.4 mA beam current
forward rf power |  |  | 
cavity 1 |  | 225 kW | 649 kW
cavity 2 |  | 250 kW | 620 kW
cavity 3 |  | 280 kW | 640 kW
cavity 4 |  | 265 kW | 625 kW
Flattop cavity |  | ~110 kW (active) | 14 kW (passive)
Total rf power | 0 kW | 1130 kW | 2548 kW
grid power |  |  | 
Anode PS 1 |  | 413 kW | 1002 kW
Anode PS 2 |  | 413 kW | 995 kW
Anode PS 3 |  | 456 kW | 1052 kW
Anode PS 4 |  | 435 kW | 1016 kW
power distribution WSGA | 181 kW | 526 kW | 533 kW
total grid power | 181 kW | 2244 kW | 4599 kW
efficiency | 0 | 0.50 | 0.55
Including all rf systems (llrf, tuning system, control system, forced air cooling, transmission line cooling, load for flattop).
Total filament power
 100kW
1.

## Slide 9: Cooling system for Tetrodes
HF0: Cooling circuit for tetrode amplifiers for the ring cyclotron
Demineralized water
Inlet temperature at tube 55°C
Outlet temperature up to 80°C
Heat recovery system ~3’357 MWh/Year
(~6.5% of energy consumption)
Suppling ¼ of heat for PSI buildings (Shutdown from Christmas to April)
1.

## Slide 10: SLS Layout and RF stations
Linac (100MeV):
Two TH2100 (35 MW max) & pfn modulator (3 GHz)
Op. since April 2000
Booster 500 MHz RF
1 Klystron power plant 180 kW (max)
Op. since July 2000
1 in house SSA power plant 65 kW (max)
Op. Since 2016
Both stations can supply the Booster cavity (ramp 2-40 kW) or be used for the RF test facility
Storage ring 500 MHz RF
4 klystron power plants 180 kW (max)
Op. since December 2000
1
2
3
4
B
Linac
SC
T
2.

## Slide 11: Layout SR 500 MHz accelerating station (large contribution to power consumption)
2.
Pulse Step Modulator: 46 kV / 7.5 A
Test 180kW CW at 45.5 kV,/ 6.5 A
60% (supplier) => operational 41-51% (not saturated & matching)

## Slide 12: Characterization power consumption SR stations (measurements on SR2)
2.
Klystron RF power: 115 kW
Grid power measurement: 261 kW
Grid to RF efficiency 44% (good Klystron)
The electronic efficiency of the klystrons fluctuates from tube to tube, and depends on a non optimal matching of the tube exit to the 50 Ohm line (cirulator) and refurbishinh history.
The best case, one klystron reuned for better matching, can reach ~50% efficincy i normal operation
Grid Power measurement at PSM input. Includes all energy consumer of the RF plant included klystron auxiliaries

## Slide 13: SLS 2 Storage Ring Upgrade & RF
2.
Storage ring 500 MHz RF
4 commercial SSA
150 kW/station maximum
124 kW/station (all ID closed)
Expected global efficiency > 56%
New BLF978P & single ended module
Drain voltage can be optimized for max efficiency at each operation point
4 HOM damped cavities in same straight section
Dark-Period 01.10.2023 - 31.12.2024
Planned commissioning with beam from January 2025
Provisional implementation layout

## Slide 14: Comparison SLS1 and SLS2
2.
Main RF-System Storage Ring |  | SLS 1 2.4 GeV – 400 mA | SLS 2.0 2.7 GeV – 400 mA
Total RF voltage | kV | 2080 | 1780
Number of cavities |  | 4 | 4
Voltage per cavity | kV | 520 | 445
Wall loss per cavity | kW | 40 | 30
RF-power/cavity with beam and max. ID Power | kW | 102 | 124
Grid to RF efficiency | % | 0.44 | 0.56
Grid Power/RF amplifier max ID Power | kW | 227.3 (909.1*) | 221.4 (885.7*)
Grid Power /RF amplifier Average ID Power | kW | 227.3 (909.1*) | 196.4 (786*)
* For 4 RF amplifier stations
Global heat recovery ~200 MWh/year
RF contribute as all other systems, low temperature => low efficiency
(~1.6% of energy consumption)

## Slide 15: Indication operational RF costs for SLS2
2.
Cost delopments assuming:
1 Kly. refurbising/20years/station
1 Kly. new/20years/station
0.1 CHF/kWh

## Slide 16: Rational behind the upgrade to SSA
2.
Motivations | 
RELIABILITY | Cope with the risk of aging and discontinued components Built-in redundancy
Phase noise | Old Station not fulfilling the SLS2 requirements (keep energy fluctuations below ID BW)
Maintenance | Modular system allows for fast maintenance / In house expertise on SSA (no HV)
Klystron availability | Only few klystron suppliers and growing costs
Grid to RF efficiency | Wasn’t the driving argument, but an improvement is expected
Operational costs | Beside better efficiency, expected low maintenance costs (klystrons)

## Slide 17: Overview RF stations in SwissFEL
0.7- 7 nm
Athos Undulators
BC 2
Linac 1
13 C-Band stations
Linac 2
13 C-Band stations
Linac 3
13 C-Band stations
Aramis Undulators
Switch
Yard
210 m
2.1 GeV
273 m
3.0 GeV
510 m
2.1- 6.1 GeV
1 (0.8) - 7 Å
S band
(2 x4 m)
Gun: 1 S-Band station
Laser-Heater
Booster 1
2 S-Band stations
BC 1
S band
(4x4 m)
X-Band linearizer: 1 station
18 m
150 MeV
80 m
320 MeV
S band
100 MV/m
Deflector
X-Band
Polarix 2 x 1 m
2.75- 3.25 GeV
399 m
Collimation
Athos Linac
1 Cband station
466 m
568 m
Deflector
C-Band
Regular operation
100 Hz repetition rate
2 Bunches / RF pulse (10 to 200 pC)
Up to 6 GeV beam energy in Aramis
S-Band: 7
C-Band: 27 => dominate power consumption
X-Band: 2
Global RF power requirement ~1.9 MW
Booster 2
2 S-Band stations
Deflectro S-Band: station
3.

## Slide 18: C-band Linac modules
four 2 m long C-band structures, 30 MV/m
240 MeV energy gain per module
9 m
C-band-klystron 5.7 GHz, 50 MW, 3 μs, 100 Hz,  43%
BOC pulse
compressor
Main LINAC + Athos | #
LINAC module | 27
Modulator | 27
Klystron | 27
Pulse compressor | 27
Accelerating structure | 108
Waveguide splitter | 81
Waveguide load | 108
Klystron modulator
370kV / 344A
3.

## Slide 19: C-Band Linac Klystron modulators
Specified for 50 MW / 3µs RF, 370kV / 344A / < 15 ppm voltage stability pulse to pulse @ 100 Hz
Two technologies (suppliers) were qualified at PSI
13 K2-3 type (Linac 3)
13 units for Linac 1 & 2 + 1 unit for the Athos Linac
Since 2019: Ampegon Power Electronics AG, founded by the group group Aretè & Cocchi Technology (OCEM)
3.
12 IGBT Switches
4.5 kV max
3.0 kA max
60 IGBT Switches
1.7 kV max
1.6 kA max

## Slide 20: Grid to RF Global Picture S-, C- and X-Band
3.
Efficiency at the nominal operational conditions at 100 Hz
 | Ampegon | Scandinova
RF FWHM (µs) | 3.0 | 
Peak RF (MW) | 37.65 | 
average RF (kW) | 11.3 | 
Power station av. Power (kW) Measured, includes auxiliaries (solenoid ~6 kW) | 57.2 | 
Grid to RF efficiency (%) Klystron efficiency 43% | ~ 20 | 
Voltage rise time 10-90% (us) | 0.77 | 1.1
Voltage fall time 90-10% (us) | 1.23 | 1.8
Nominal for 240 MeV energy gain

## Slide 21: Heat recovery
3.
Original Design
Body
Bellow for thermal stress reduction
Collector
~80 °C to
Heat recovery
Modification of klystron agreed with Supplier
Global heat recovery ~2’600 MWh/year
(~11% of energy consumption)

## Slide 22: Rational/priorities behind power source design
3.
Priorities | 
RELIABILITY | Keep the components between safety margin => large number of sources increases probabilities of failures and shot to shot deviations
Pulse to pulse stability | Essential for pulse to pulse FEL stability (1e-4 energy, fs arrival time, peak current, …) => reached < 10 ppm
Maintenance | Modular system and reasonable HV
Klystron | Allow for hot collector operation (90 °C) & energy recovery
Grid to RF efficiency | Wasn’t a driving argument

## Slide 23: Wir schaffen Wissen – heute für morgen
Many thanks to:
M. Schneider (HIPA),
L. Stingelin (SLS)
J. Alex (SwissFEL)
D. Reinhard (Building services)
M. Jörg (Infra. & el. inst.)
For providing material for this presentation

## Slide 24: Resereve Material

## Slide 25: PSI
Basel
49 km
bird's-eye view
Zurich
30 km
bird's-eye view
CERN
220 km bird's-eye view

## Slide 26: Operation parameters Ring rf without beam
 |  | cavity 1 | cavity 2 | cavity 3 | cavity 4 | flattop cavity
gap voltage | kVp | 782 | 844 | 848 | 882 | 454
1MW P forward | kW | 225 | 250 | 280 | 265 | 110
1MW P reflected | kW | 17 | 16 | 20 | 17 | 9.9
VSWR |  | 1.76 | 1.68 | 1.73 | 1.68 | 1.86
100kW P forward | kW | 7 | 7.5 | 6 | 6 | 6.5
100kW P reflected | kW | 0.2 | 0 | 0.2 | 0.1 | 0.09
1MW P in driver | kW | 6.8 | 7.5 | 5.8 | 5.9 | 6.41
1MW P produced | kW | 218 | 243 | 274 | 259 | 104
1MW U Anode | kV | 15.9 | 15.9 | 16.5 | 16 | 11.5
1MW I Anode | A | 23.8 | 23.3 | 25.4 | 25.4 | 16.6
1MW P Anode DC | kW | 378 | 370 | 419 | 406 | 191
1MW Anode PS 16kV grid power | kW | 413 | 413 | 456 | 435 | 
tetrode cooling water inlet temperature | °C | 53.6 | 53.5 | 53.7 | 53.4 | 54.8
tetrode cooling water outlet temperature | °C | 66.6 | 63.8 | 65.3 | 63.9 | 66.9
tetrode cooling water delta temperature | °C | 13.0 | 10.3 | 11.6 | 10.5 | 12.1
tetrode cooling water flow rate | l/min | 213 | 227 | 221 | 231 | 112
P calorimetric | kW | 194 | 163 | 179 | 170 | 95
efficiency RF/DC |  | 0.58 | 0.65 | 0.65 | 0.64 | 0.54
efficiency RF/AC 16kV Mains |  | 0.53 | 0.59 | 0.60 | 0.60 | 
1.

## Slide 27: Operation parameters Ring rf with beam 2.4mA
 |  | cavity 1 | cavity 2 | cavity 3 | cavity 4 | flattop cavity
gap voltage | kVp | 844 | 842 | 846 | 889 | 553
1MW P forward | kW | 649 | 620 | 640 | 625 | 36
1MW P reflected | kW | 22.5 | 32 | 21 | 30 | 22
VSWR |  | 1.46 | 1.59 | 1.44 | 1.56 | 8.16
100kW P forward | kW | 35 | 35.5 | 34 | 34 | 0.4
100kW P reflected | kW | 1.2 | 0.05 | 1.1 | 1.5 | 0.4
1MW P in driver | kW | 33.8 | 35.45 | 32.9 | 32.5 | 0
1MW P produced | kW | 615 | 585 | 607 | 593 | 36
1MW U Anode | kV | 15.9 | 15.9 | 16.5 | 15.9 | 11.5
1MW I Anode | A | 57.1 | 55.7 | 58.3 | 57.7 | 4.8
1MW P Anode DC | kW | 908 | 886 | 962 | 917 | 55
1MW Anode PS 16kV grid power | kW | 1002 | 995 | 1052 | 1016 | 
tetrode cooling water inlet temperature | °C | 54.2 | 53.6 | 54.2 | 54.1 | 55.3
tetrode cooling water outlet temperature | °C | 79.7 | 77.4 | 79.1 | 76.2 | 60.4
tetrode cooling water delta temperature | °C | 25.5 | 23.8 | 24.9 | 22.1 | 5.1
tetrode cooling water flow rate | l/min | 210 | 220 | 219 | 228 | 107
P calorimetric | kW | 374 | 367 | 382 | 353 | 38
efficiency RF/DC |  | 0.68 | 0.66 | 0.63 | 0.65 | 0.65
efficiency RF/AC 16kV Mains |  | 0.61 | 0.59 | 0.58 | 0.58 | 
1.

## Slide 28: RingCyclotron: Operation Flattop
@ 0 mA (active cavity operation)
@ 2.4 mA (~passive cavity operation)