## Slide 1
Technical Infrastructure Monitoring
Service Overview

## Slide 2
Service Overview
Datatag & Alarm Configuration
Process, Equipment & Sub-Equipment
JMS Brokers
Ecosystem
2
TIM – Service Overview
TIM: Summary

## Slide 3
2
TIM – Service Overview
TIM: Overview
HelpAlarm
NxCALS
Oracle
Grafana
Elasticsearch
Redundant
Servers
Data
Acquisition
DIP
CMW
…
Clients
TIM Viewer
HelpAlarm
DIP Publisher
…
TIM / C2MON
Server
JMS (ActiveMQ)
JMS (ActiveMQ)
OPC
Monitoring service based on C2MON (CERN Control and MONitoring platform) framework
Receives data tags and alarms from multiple heterogeneous systems and propagates them to client applications
Configuration
MODESTI

## Slide 4
3
TIM – Service Overview
TIM: Overview
CSAM Alarms
CERN Guards
TI Operators
Access System
ATLAS SLIMOS
CRYO Systems
Electrical Grid (2018)
Computer Center
Follow-up of major incidents with expert groups
Alarm details (Single Alarm Page)
TIM
HelpAlarm
Monitoring service based on C2MON (CERN Control and MONitoring platform) framework
Receives data tags and alarms from multiple heterogeneous systems and propagates them to client applications
Critical service: main tool used by BE-OP-TI (CCC) for monitoring Technical Infrastructure and critical applications

## Slide 5
Monitoring service based on C2MON (CERN Control and MONitoring platform) framework
Receives data tags and alarms from multiple heterogeneous systems and propagates them to client applications
Critical service: main tool used by BE-OP-TI (CCC) for monitoring Technical Infrastructure and critical applications
Used by:
  Different access groups to monitor their equipment and send alarms
  Software solution for SPS Personal Protection System (SPS-PPS)
  Alarm gateway for CERN Safety Alarm Monitoring System (CSAM) & WinCC OA
  SPECTRUM Network alarms
5
TIM – Service Overview
TIM: Overview

## Slide 6
Web application to add/remove/modify data tags and alarms in TIM
Plugin-based, provides customizable workflows (BPMN 2.0, Activiti) for multiple domains (CSAM, TIM, WINCCOA, PSEN, SPECTRUM, RULES)
6
TIM – Service Overview
TIM: Datatag & Alarm Configuration (MoDESTI)

## Slide 7
Web application to add/remove/modify data tags and alarms in TIM
Plugin-based, provides customizable workflows (BPMN 2.0, Activiti) for multiple domains (CSAM, TIM, WINCCOA, PSEN, SPECTRUM, RULES)
Datatag & Alarm information as Metadata
7
TIM – Service Overview
TIM: Datatag & Alarm Configuration (MoDESTI)

## Slide 8
Web application to add/remove/modify data tags and alarms in TIM
Plugin-based, provides customizable workflows (BPMN 2.0, Activiti) for multiple domains (CSAM, TIM, WINCCOA, PSEN, SPECTRUM, RULES)
Datatag & Alarm information as Metadata
Visualization & Filtering in Grafana using Metadata
8
TIM – Service Overview
TIM: Datatag & Alarm Configuration (MoDESTI)

## Slide 9
TIM DAQs: Process, Equipment, Sub-equipment
A Process represents a single Data Acquisition Process (DAQ)
An Equipment is a piece of physical sensory hardware, or any other kind of data source (middleware service or DB). A Process can have one or more Equipments.
A Sub-Equipment is a logical separated data source withing an Equipment. An equipment can optionally contain one or more Sub-Equipments.
1..n
0..n
TIM – Service Overview
Source: https://c2mon.web.cern.ch

## Slide 10
TIM DAQs: Process, Equipment, Sub-equipment
Process / equipment monitoring
StatusTags, AliveTags, CommFaultTags: Monitoring the connection between:
    DAQ and Server
    DAQ and data source
Command tags: Start, stop, restart DAQ process remotely
DataTags:
    Belong to Equipments/Sub-equipments
    Some datatags (Boolean) can also be alarms
1..n
0..n
TIM – Service Overview
A Process represents a single Data Acquisition Process (DAQ)
An Equipment is a piece of physical sensory hardware, or any other kind of data source (middleware service or DB). A Process can have one or more Equipments.
A Sub-Equipment is a logical separated data source withing an Equipment. An equipment can optionally contain one or more Sub-Equipments.
Source: https://c2mon.web.cern.ch

## Slide 11
TIM: JMS Brokers
JMS Brokers
    DAQ JMS: One JMS queue per DAQ instance
    Client JMS: One JMS topic per DAQ instance
DAQs
Servers
Clients
DAQ JMS (Queues)
Client JMS (Topics)
TIM – Service Overview

## Slide 12
TIM: JMS Brokers
JMS Brokers
    DAQ JMS: One JMS queue per DAQ instance
    Client JMS: One JMS topic per DAQ instance
Special case: WinCC OA
    Redundant alarm-legacy-acceptor transforms old SonicMQ format to ActiveMQ compatible JMS message.
    Data is sent to alarm legacy topics. One topic per project.
    Alarmsource DAQ is subscribed to alarm legacy topics. Performs filtering and alerting if unknown alarms are received.
    Data is sent as Datatag message via JMS queue to C2MON
DAQs
Servers
Clients
DAQ JMS (Queues)
Client JMS (Topics)
WinCC OA
alarm-legacy-acceptor
alarmsource DAQ
1
2
1
3
4
TIM – Service Overview

## Slide 13
12
TIM: Ecosystem
TIM – Service Overview

## Slide 14
<número>
TIM: Questions
TIM – Service Overview