## Slide 1
VACUUM ALARM SYSTEMS
André Rocha
TE-VSC-ICM

## Slide 2
Content
Overview Alarm Systems used in the Vacuum Control System
LASER alarms
  Configuration architecture
  Configuration DB data model
  Configuration using vacuum framework database engineering tool
Vacuum Alarm Panel
  Basic Functionality
  Architecture
Vacuum User Notifications
  Basic Functionality
  Architecture
Conclusions
2

## Slide 3
LASER ALARMS
Graphical Representation
UI Separated from vacuum SCADA
Offline configuration
For accelerator operations (CCC)
VACUUM ALARM PANEL
Graphical Representation
Directly accesible from vacuum SCADA
Can be changed at runtime
For vacuum operations
USER NOTIFICATIONS
No Graphical Representation
Rely on email servers
Can be changed at runtime
For vacuum operations
DEFAULT ALARMS
USER ALARMS
ALARM SYSTEMS IN VACUUM
Defined by Machine Responsibles
Defined by Users
3

## Slide 4
SCADA
SPS
CPS
LHC
VACUUM AND LASER ARCHITECTURE
LASER configuration
LASER Manager
S7
vacCC Exporter
LASER CONFIG
Master
DP CONFIG
Datapoints
Import
LASER
vacCC Master
vacCC Machine
Alarm attributes
4
vacFW DB engineering tools

## Slide 5
LASER CONFIGURATION IN VACUUM
Configuration is fully automated
When a device is added to the control system using the Vacuum Controls Configurator, LASER configuration is automatically generated without any user input.
The user may only choose to override where the alarm is published (alarm category)
5

## Slide 6
LASER CONFIGURATION DB MODEL
Vacuum Device
Fault Family: VAC_PRESSURE_{machine}
Fault Member: {mainPart}_{sector}_{eqp}
Fault Code: 2
Description: Device is in error
Fault Family: VAC_PRESSURE_{machine}
Fault Member: {mainPart}_{sector}_{eqp}
Fault Code: 1
Description: Device is OFF
Fault Family: VAC_PRESSURE_{machine}
Fault Member: {mainPart}_{sector}_{eqp}
Fault Code: 3
Description: Pressure Too High
Control Type
Datapoint type
Datapoint Elements
Alarms
Alarm Attributes
AL1
AL2
AL3
VG_P9
VG_P9
Device OFF
Device Error
High Pressure

## Slide 7
LASER ALARM DECLARATION
Default configurations in Vacuum Controls Configurator Master
Declaration of alarms
Declaration of alarm attributes
  Some attributes depend on context
  FM: {mainPart},{eqp} will be replaced during export of configuration as LSS2, VVGST.3.6R2.R
7

## Slide 8
LASER ALARM DECLARATION
Association of alarms to Datapoint Elements
Boolean datapoint elements can be associated with alarm instances
Device developers specify which datapoint element and bit contains the alarm
8

## Slide 9
LASER ALARM DECLARATION
9

## Slide 10
VACUUM ALARM PANEL
Developed for the VELO SCADA application
  User request to have alarm panel inside the application due to the complexity of the process
  Generic, pure WinCC-OA alarm panel – no dependency on any database / framework
Basic functionality
  Supports Digital Boolean Calculated
    Alarm tracks single bit from source word
  4 alarm status: active, not active, acknowledged, went
  Alarm Priority
    Different color displayed in alarm panel
    Sorting
Intended to be a temporary solution
Not Active
Active
Acknowledged
Went
Alarm bit = 1
Alarm bit = 0
User ack
Alarm bit = 0
User ack
Alarm bit = 1
10

## Slide 11
11

## Slide 12
VACUUM ALARM PANEL ARCHITECTURE
Alarm Configuration Panel
Boolean Calculated Alarm Engine
(Control Manager)
Calculates alarm statuses from raw datapoints
WinCC-OA Alarm Datapoints
WinCC-OA Process Datapoints
Create/edit/delete
Subscribe to changes in source DPEs
Alarm Panel
Subscribe to configuration / ack
Subscribe
ack
Write alarm status
12

## Slide 13
VACUUM USER NOTIFICATIONS
Allows users to have individualized notification configurations
Advanced alarm scoping:
  Machine mode (RUN, STEADY, PROTON RUN, MD, etc..)
  Device type (Gauge, Valve, Controller, etc)
  Alarm Criteria (depends on device type)
  Location scope (Global, Main Part, Sector)
Filtering on:
  Minimum duration
  Hystheresis
  Number of messages (Grouping)
Email based
13

## Slide 14
C++ Library
Functional Types
Functional Type Alarm Criteria
Usernotifications.ctl
(Control Manager)
WinCC-OA Configuration
WinCC-OA Process Datapoints
Create/edit/delete
Subscribe
Subscribe
USER NOTIFICATIONS ARCHITECTURE
Send email
User Notification Configuration
Notification Config
Criteria(Eqp, sector, criteria)
List of equipment
Message Pool
Filtering
Grouping
isOf type
dpeChange
getMessageQueue
checkCriteria()
Eqp
criteriaMatch
createConfig
14

## Slide 15
Conclusion
3 Different alarm systems coexist in the vacuum control system to meet the needs of different users:
  LASER:
    CCC Operators
    Offline automated configuration via vacFW DB engineering tool
    System alarms defined by equipment type developers
  Vacuum Alarm Panel
    Vacuum Operators
    Online manual configuration
    System alarms defined by system administrator
    Future work: replace this with generic alarm panel solution of BE-ICS
  User notifications
    Offer high level of customization
    Vacuum operators
    Online manual configuration
    Alarms defined by users
15