## Slide 2: HSE Seminar: Exploiting data of the Radiological and Environmental Monitoring System
CERN HSE Unit
A. Ledeul, G. De La Cruz, F. Malacrida, M. Widorski, J. Regnard, C. Chiriac, H. Boukabache

## Slide 3
Introduction

## Slide 5
How to make sense of this ?

## Slide 6: Context
From Instrumentation to Operation
CERN Control Centre
Experiments Control Rooms
Safety Control Room
WATER
VENTILATION
AIR
WEATHER
OPERATIONAL RADIATION PROTECTION
CONTAMINATION
GATE
Radiation Protection & Environmental Experts
Commands
On, Off, Sample, etc.
Parameters
Thresholds, Units, etc.
Measurements
Alarm signals
Faults
Process Statuses
50k parameters
120k defined alarms
10M meas./hour
800 synoptic
REMUS
Supervision
Control
Data Acquisition
ERGO Data Visualization
300 active users
REMS = Radiological and Environmental Monitoring System
REMUS = Radiation and Environment Monitoring Unified Supervision
ERGO = Environment and Radiation Graphic Observer
SCADA = Supervisory Control and Data Acquisition
800 stations

## Slide 7: Problem Statement
From Data to Information
REMUS Data in Numbers
1,000,000 online variables
50,000 remote parameters
90,000,000,000 measurements / year
Alerts to Control Rooms
Reports to host state authorities
Data analysis
Dashboards
Aggregated statistics
Predictive maintenance
Anomaly detection

## Slide 8: REMADS Project (2019-2021)
Integrated in HSE RAMSES Program
REMADS = REMus Analytics and Data Services
GPN = General Purpose Network
LAN = Local Area Network
LoRaWAN = Long Range Wide Area Network
NXCALS = Next CERN Accelerators Logging Service
EAM = Enterprise Asset Management
6 months discussions with REMS Users
User Requirement Specification
Project Proposition
  REMUS Web
  Data Analysis toolbox
  Portable system for on-site intervention
  ERGO 4.0
  Complex transformation operations on Trends
  InforEAM Integration
  Maintenance Management
  Information System
  REMUS GPN
  Secured GPN LAN/Wifi/4G/LoRaWAN connectivity
4G
  CERN data-stores
  Integration with Kafka and Hadoop (NXCALS)

## Slide 9: Collaboration with other Departments
Data
CERN-wide services used
Data Streaming Platform
Transmit Real-Time data out of REMUS
Managed by IT
Big data technologies
Centralizes CERN accelerator data
Managed by BE
Time Series Database
Buffer Real Time data
Managed by IT
Apache Kafka®:
open-source distributed streaming platform
NXCALS
Source: NXCALS - Architecture and Challenges of the Next CERN Accelerator Logging Service,
J. Woźniak and Chris Roderick, 2019
Long Term Storage
Near-Real Time
NXCALS = Next CERN Accelerators Logging Service

## Slide 10: Why & How to use the newly available Software Tools ?
Use-cases & Demos
Data Analysis using SWAN Speaker: Hamza Boukabache (HSE-RP)
REMUS Web
Speaker: Gonzalo De La Cruz (HSE-TS)
Dashboards
Speaker: Fabrice Malacrida (HSE-RP)
Statistics & Reporting
Speaker: Markus Widorski (HSE-RP)
NXCALS & TIMBER
Speaker: Catalina Chiriac (HSE-TS)
InforEAM & HelpAlarm
Speaker: Julien Regnard (HSE-ENV)
HSE
HSE
HSE
IT & BE
BE
EN & BE

## Slide 11
REMUS Web

## Slide 12
Dedicated platform for the analysis and exploitation of REMUS data.
Goals:
  Facilitate access to REMUS data.
  Provide data analysis tools for REMUS users.
  Transform REMUS data into meaningful information.
REMUS Web

## Slide 13
REMUS Web Key Features
Remote access to REMUS data from any desktop or mobile devices.
Powerful tool for the creation and visualization of Dashboards.
Tailor-made data analysis and data extraction tools for Radiation and Environmental protection experts
Generation of domain-specific reports for internal analysis and to report to CERN’S host states authorities.

## Slide 14
Demo
  https://remus.cern.ch

## Slide 15
REMUS Web Dashboards

## Slide 16
Demo
  https://remus.cern.ch/PROD/dashboards/645
  https://remus.cern.ch/PROD/dashboards/502
  https://remus.cern.ch/PROD/dashboards/844

## Slide 17
REMUS Web Statistics & Reporting

## Slide 18
EDMS no: 2746071

## Slide 19
EDMS no: 2746071

## Slide 20: Statistics  Channels / Events
Retrieve monitor/channel names and types in a specific area
Access the EAM links to a specific measurement position
Create statistics on specific types of events (alarms, faults): Listing and aggregating
EDMS no: 2746071

## Slide 21
EDMS no: 2746071

## Slide 22
EDMS no: 2746071

## Slide 23
EDMS no: 2746071

## Slide 24: Reporting  Measurement / Parameter / Snapshot
Get summary statistics of measurements on a group of channels for extended periods
Check parameters settings of a groups of channels for quick validation or comparison
Reporting specific for control measurements (HFM, Portal monitors) to generate statistics on number and results of controls
EDMS no: 2746071

## Slide 25
Measurement reporting
EDMS no: 2746071

## Slide 26
Parameter reporting
EDMS no: 2746071

## Slide 27
Snapshot reporting
EDMS no: 2746071

## Slide 28
Demo
  https://remus.cern.ch/PROD/reporting
  https://remus.cern.ch/PROD/statistics

## Slide 29
InforEAM & HelpAlarm

## Slide 30
InforEAM & HelpAlarm
InforEAM
EN
HSE
130 Environmental Monitoring Stations
125 Mi datapoints / year
2200 pieces of equipment declared
750 Preventive maintenance activities / year planned
Fully operational by October 2022
No possibility to aggregate the maintenance activities by MS/Channel
SharePoint will be obsolete soon
…
Since 2009

## Slide 31
InforEAM & HelpAlarm
Preventive maintenance activity

## Slide 32
InforEAM & HelpAlarm
https://cmmsx.cern.ch/SSO/eamlight/position/PEMWM01=3876

## Slide 33
InforEAM & HelpAlarm
BE
HelpAlarm
InforEAM
EN
HSE
160 Environmental Monitoring Stations
125 Mi datapoints / year
750 Preventive maintenance activities / year
90 alarms requiring immediate intervention

## Slide 34
Demo
  https://helpalarm.cern.ch
  https://cmmsx.cern.ch/SSO/eamlight

## Slide 35
REMUS data in NXCALS/TIMBER

## Slide 36
NXCALS
TIMBER Web
Data Sharing to NXCALS
HSE-CEN
HSE-RP
BE-OP
EP
Notes: Industrial Controls (QPS, Cryo, Vacuum, etc.) CMW (Beam Instrumentation, RF, Beam Transfer, Powering, etc.) Many special cases (Fundamentals, Converters, LHC Fills and Beam Modes, etc.)

## Slide 37
Shared Big Data storage of all CERN control systems
Help in beam observation devices and investigate problems with accelerator equipment or unexpected beam behavior.
Keep data for long period of time and assure good and performant analyses and data extraction by the physicists.
CERN Control Center
NXCALS System
EDMS no: 2746071

## Slide 38
Demo
  https://timber.cern.ch

## Slide 39
Data Analysis using SWAN (NXCALS data)

## Slide 40
Plastic Air filled ionization chamber
High Radiation Area
Low Radiation Area
SPA6 cable
Conceptual view of CROME at CERN
Bulk
Rackable
1000V
100fA
CROME Rack at EHN1 (North Area)
Uninterruptible Power Supply
Includes a battery for continuous operation
Radiation Monitoring and processing units
Up to 1km
CROME Junction Box
CROME System
Data Analysis using SWAN (NXCALS data)
CERN Radiation Monitoring Electronics (CROME)
Two configurations :

## Slide 41
CERN - Radiation & Environmental Monitoring System
650 Radiation Protection and Environmental monitoring devices
AWAKE
LHC
CTF3
AWAKE
n-TOF
LINACs
East Area
LHC injectors
North Area
SPS
PS
AD
TTs
HIE-ISOLDE
CROME
CROME
1984
2004
2021
2028
Self production capabilities
Tests / validation inside climatic chambers
Assembly Workshop
For more info : https://crome.web.cern.ch/node/35
CROME System
Data Analysis using SWAN (NXCALS data)

## Slide 42
42
12 Ethernet connections
6 Ethernet connections
IT Socket
IT Socket
IT Socket
CROME Radiation Monitor
CROME Radiation Monitor
1 Eth connection
1 Eth connection
1 Eth connection
IT Socket
IT Socket
Technical Network
Maintenance
CERN Control Room
Real Time Measurements
Events
Status
Historical Values
Real Time Measurements
Events
Status
Historical Values
Real Time Measurements
Events
Status
Historical Values
Real Time Measurements
Events
Status
Historical Values
CERN NTP Servers
Status
ECA4 - SPS
CROME/REMUS Network
CROME System
Data Analysis using SWAN (NXCALS data)

## Slide 43
CERN Technical Network
Dose rate
Integrated doses
Temperature
Humidity
High voltage
Events
Statuses
NXCALS
Operational Data
Injection
CMPU – Rack Electronics
Wired CROME radiation detectors
Wireless CROME rad. det.
TIM
Internal Voltages
Internal Temperatures
SoC internal parameters
…
Injection
Non-Operational Data
CROME System
Data Analysis using SWAN (NXCALS data)

## Slide 44
Currently: Data sent to NXCALS remains unused
Goal: Use data on NXCALS for Predictive Maintenance
Develop Anomaly Detection process to identify failure precursors
CROME System
Data Analysis using SWAN (NXCALS data)
Work Package Overview

## Slide 45
No System Failures known
No data available that represents healthy state of system
No definition of anomalous behavior
Anomalies are rare and different
Focus on noise in signals
Use multi-level wavelet transform (MRA-WT) for noise extraction
CROME System
Data Analysis using SWAN (NXCALS data)
Challenges for Anomaly detection

## Slide 46
NXCALS
CROME Internal Data
Pre-Processing:
Feature Engineering: Calculate statistical features (raw and extracted noise signal)
Handling of Missings
Scaling
Optional
Apply Algorithms:
Isolation Forest, Autoencoder
CROME System
Data Analysis using SWAN (NXCALS data)
Anomaly Detection Process
Being evaluated

## Slide 47
NXCALS
Training data
Model training
e.g. AE
Operational
Calculate anomaly scores
Sample | Anomaly score
PMIST214 | 8.564
PMINA0603 | 4.371
PAXNT211 | 2.093
… | …
Ranking
Manual analysis
Assign Label
Normal
Anomaly
Maintenance?
Retrain Model
+ Internals?
Daily, Weekly, …
CROME System
Data Analysis using SWAN (NXCALS data)
Preliminary Architecture
Feedback Loop

## Slide 48
Demo
  https://swan.cern.ch
Find the tutorial here : https://gitlab.cern.ch/hboukaba/nxcals/

## Slide 49
Conclusion

## Slide 50: Summary
Evolutions necessary for the operation
REMUS Web
  REMUS data analysis gateway
REMUS Web Dashboards
  Share data summary with other
REMUS Web Statistics & Reporting
  Efficiently generate reports for analysis and reporting
InforEAM & HelpAlarm
  Interface CERN-wide Maintenance and Alarm systems
REMUS data in NXCALS/TIMBER
  Long term Data storage at high resolution
  Allow comparison and correlation with other control systems’ data
REMUS data in NXCALS/SWAN
  Extended big-data analysis capabilities

## Slide 51: What’s next? : REMUS Web Application Editor
Ease REMUS Application Edition

## Slide 52: What’s next? : Net Ambient Doses and Releases Reports
A step further into Knowledge Integration
Streamline the generation of adjusted Ambient Doses and Releases Reports
  Increase reliability of data treatment
  Minimize risk of human error
  Guaranty repeatability and traceability
Net Ambient Doses and Releases Reports functional specifications.
Credit: F. Malacrida (HSE-RP)

## Slide 53: A glimpse into the future
Other CERN Web Technologies Projects for Control Systems
Growing trend in Industrial Control Systems at CERN and beyond
CTTB Working group
  Web Technologies task Force
W.R.A.P. (BE-CSS)
  Cross-system live charts
Flow Project (EN-SMM/BE-CEM)
  Live web widgets
CTTB = ATS Common Hardware & Software Technologies Technical Board
WRAP = Web Rapid Application development Platform
WRAP. Credit: BE-CSS
Flow Project. Credit: BE-CEM

## Slide 54
Thank you!

## Slide 55
Questions