## Slide 1: Infrastructure/Integration/Schedule constraints
A. Rossi with contributions from M. Modena , P. Fessia, J. Oliveira, G. Aparicio Cantalapiedra, S.Maridor, Y. Thurel, M. Martino, G. Girardot.
WP2/WP13 HL-LHC Satellite Meeting, Uppsala 2022 - Long-Range Beam-Beam Wire

## Slide 2: HL-LHC space reservation
A space reservation of 4.5 m on both beams was made on either sides of IP1/5 = 1 unit per beam per location, in cell 5 (between Q4 and Q5)
Space for racks

## Slide 3: HL-LHC space reservation
(similar for IP5)

## Slide 4: HL-LHC galleries - “UR Option”
core
UR no-radiation area
LHC
PC in the new technical gallery UR and cables routed through : UR  UA  cores  LHC  BBLR

## Slide 5: HL-LHC galleries - “UR Option”
core
BBLRC
PC in the new technical gallery UR and cables routed through : UR  UA  cores  LHC  BBLR
Pro-1 : Finding/building converters of 150A x 60-70V* rating is feasible with commercial units.
Pro-2 : Space for racks already reserved.
Con-1: It is not possible to use any existing core: devoted to RF flexwell (fragile) cables, and not to share signal cables with power cables.
Con-2: Heat losses to be managed around the core location. Split Air Conditioner may be required - study to be done.

## Slide 6: HL-LHC galleries - “UR Option”

## Slide 7: HL-LHC galleries - “RR Option”
BBLRC
PC in the LHC RR alcoves and cables routed through : RR  BBLR
RR (radioactive areas)
Con-1 : This would require new radiation tolerant design converters. Effort (design) for only few units (#8).
Con-2 : Need to find place in RR(1/5), not studied here.
Pro-1 : No need to install DC power cables from tunnel up to UR.

## Slide 8: Powering: series recommended
Chart: Current [A]
| 30 | 60 | 90 | 120 | 150 | 180
1mm_AIR | 0.5527 | 1.133 | 1.76 | 2.503 | 3.372 | 4.689
1mm_VACUUM | 0.5615 | 1.131 | 1.784 | 2.486 | 3.435
Bertarelli et. al, Special Joint HiLumi WP2/WP5 Meeting
22.02.2022
~12V/m
@150A, 14Vx3+10V (voltage drop for cabling)
52V
Y. Thurel

## Slide 9: Powering: series recommended
@150A, 14Vx3+10V (voltage drop for cabling)~60V
Y. Thurel
Ballpark figures:
1 rack with 2 converters of 12 kWatts each ≃ 60 kCHF => 240 kCHF
  (1 rack with 1 converters of 18 kWatts each ≃ 50 kCHF => 400 kCHF)
Cabling expected ≃ 500 kCHF (to be confirmed)

## Slide 10: Schedule constraints
Cabling should be ideally implemented in the same campaign as for the rest of HL-LHC (LS3)
  If the power cable have to go in the same core as the RF cables, we should install them before (hybrid solution with bas-bars?) so to minimise impact on RF cables. Thermal studies to be done.
  If HL-LHC chooses to add another core (review in Nov. 2022), time may be more relaxed, but it would be less expensive/more efficient to do it at LS3.