## Slide 1: Conductor needs – HTS T&D Cables
Critical current >1 kA/cm width at 70 K (higher is beneficial)
Long lengths needed to minimize splices (1 km/piece or longer)
Low contact resistance coating (solder coating or smooth cu-surface)
Performance in magnetic field performance is not important
Operating temperature 65 – 70 K for 2GHTS; 20 K for MgB2
Piece lengths: >500 m or longer
Stabilizer for stability (Resistive stabilizer for FCL cables)
Low cost because cables need is large volume (40 x cable length)
Cost targets for cable systems including conductor TBD

## Slide 2: Conductor needs – SMES
Critical current >2 kA at 4 T, 20 K (to use single stage cryocoolers)
Wires/cables/bundles with current sharing built-in
Long length cables needed to minimize splices (1 km/piece or longer)
Operating temperature >20 K for 2GHTS; 15 K for MgB2
Piece lengths: >1 km or longer
Stabilizer for stability
Low cost because SMES needs 20 km or lager volume
Mechanical strength is critical
Conductor needs to have low ac losses for heavy-duty charging/discharging
Cost targets for cable systems including conductor TBD

## Slide 3: Conductor needs – Rotating Machines DC Field Coils)
Wires/cables/bundles with current sharing built-in
LTS is competitive here
Long length cables needed to minimize splices (1 km/piece or longer)
Engineering current density >0.2 kA/mm2 at 6 T at operating T (higher is beneficial)
Operating temperature 4-20 K for 2GHTS; 15 K for MgB2
Piece lengths: >3 km or longer
Stabilizer for stability
Low cost because machines need 100 kA-km/10 MW
Mechanical strength is critical
Conductor needs are for DC operation

## Slide 4: Conductor needs – Rotating Machines AC Stator Coils)
Operating current >3 kA at 4 T, 20 K (to use single stage cryocoolers)
Wires/cables/bundles with current sharing built-in
Long length cables needed to minimize splices (1 km/piece or longer)
Operating temperature >20 K for 2GHTS; 15 K for MgB2
Piece lengths: >1 km or longer
Stabilizer for stability
Low cost because machines need 100 kA-km/machine
Mechanical strength is critical
Conductor needs to have low ac losses for heavy-duty charging/discharging
Cost targets for cable systems including conductor TBD