## Slide 1
Moving complexity from hardware to software
…and other ideas from hardware people
Konstantinos Papastergiou
Electrical Power Converters Group – SY Dept.
Many thanks to Ivan, @EfficiencyThinkTank, Valerie, Verena, Francesco, Alex, Nikos, Dipanwita, Charles, Remi, Timm, Krister, Stephane, Raul
Joint Accelerator Performance Workshop, December 2022 Session 7: Efficiency, reliability and tools across the complex

## Slide 2: Summary
Powering of accelerators and the need for efficiency metrics
  Energy intensive processes and hidden operating costs
  An example of KPI for equipment utilisation
Addressing hardware problems with software
  from dc to cycling in transfer lines (eliminate dc operation)
  Addressing the magnetic field reproducibility issue
  Addressing consolidations needs with a fresh view
Ideas for the future Mega-accelerators and concluding remarks
  Containerisation & orchestration
  Digital embryos/twins as (early-stage) feasibility and operation tools

## Slide 3: The electrical system overview
accelerator
5-20% waste
1% waste
1-4%
waste
1-2%
waste
60-70%
no-load/always-on power losses

## Slide 4: Efficient use of energy: Getting there
CERN level:
Plan consumption
Key performance indicators
Operations/Experts:
Resources
Raise awareness
Monitor what matters
Perform data analysis
Start over 
Slide of Nicolas Bellegarde, Towards ISO50001 certification at CERN, https://indico.cern.ch/event/1193771/

## Slide 5: An example of an “expert” KPI
Objective
raise awareness about energy & and equipment life consumption
Indicator
percent % of used magnetic cycles
Example with data extracted with pyTimber for the month of August:
Using SPS mains (RPPEL.BA3.MBI) timeseries
and BCT (SPS.BCTDC.41435) timeseries
to evaluate use of SPS mains (beam time, wasted cycles, etc)

## Slide 6: Accelerator time usage
Chart: SPS Mains cycling hours in August 2022
 | 14.5347 | 19.5967 | 23.4527 | 23.4227 | 23.517 | 22.8127 | 22.5957 | 19.0887 | 23.7703 | 22.0193 | 22.747 | 23.4813 | 23.65 | 23.565 | 23.546 | 20.5903 | 15.9077 | 23.709 | 21.8187 | 23.7267 | 23.7883 | 23.3857 | 23.9723 | 23.9987 | 23.785 | 23.118 | 20.868 | 21.904 | 23.999 | 23.867 | 18.1237
Chart: Beam Vs no-beam in Ring in August 2022
Mains cycles with beam in ring | 8.0977 | 11.152 | 15.1123 | 15.5133 | 17.0807 | 16.3937 | 14.6983 | 13.03 | 16.8677 | 14.0043 | 15.378 | 16.7377 | 16.8627 | 17.3967 | 14.6173 | 12.0657 | 11.121 | 17.044 | 15.2173 | 17.169 | 17.3217 | 17.4983 | 18.5887 | 16.2807 | 17.248 | 17.206 | 14.368 | 16.216 | 18.492 | 18.5447 | 10.9327
Mains cycles without beam | 6.437 | 8.4447 | 8.3403 | 7.9093 | 6.4363 | 6.419 | 7.8973 | 6.0587 | 6.9027 | 8.015 | 7.369 | 6.7437 | 6.7873 | 6.1683 | 8.9287 | 8.5247 | 4.7867 | 6.665 | 6.6013 | 6.5577 | 6.4667 | 5.8873 | 5.3837 | 7.718 | 6.537 | 5.912 | 6.5 | 5.688 | 5.507 | 5.3223 | 7.191
Utilisation 92.5% of time in month
Beam 64.3%
of time in month

## Slide 7: Energy usage
Chart: Potential for Accelerator time gains: Degauss and Waste cycles
Degaus cycles (3.6sec, no beam) | 2.257 | 2.799 | 5.415 | 5.288 | 5.111 | 5.018 | 5.402 | 3.639 | 5.67 | 5.357 | 5.16 | 5.553 | 5.53 | 5.328 | 3.481 | 1.514 | 3.037 | 5.242 | 5.02 | 5.539 | 5.482 | 3.649 | 3.974 | 4.36 | 5.312 | 4.789 | 4.789 | 4.653 | 4.364 | 4.172 | 3.003
Waste cycles | 4.18 | 5.6457 | 2.9253 | 2.6213 | 1.3253 | 1.401 | 2.4953 | 2.4197 | 1.2327 | 2.658 | 2.209 | 1.1907 | 1.2573 | 0.84033 | 5.4477 | 7.0107 | 1.7497 | 1.423 | 1.5813 | 1.0187 | 0.98467 | 2.2383 | 1.4097 | 3.358 | 1.225 | 1.123 | 1.711 | 1.035 | 1.143 | 1.1503 | 4.188
Chart: Potential cost cutting: Degaus and Waste cycles assuming cost 90Eur/MWh
Degauss cycle (3.6sec, no beam) | 871.1596 | 1080.3614 | 2090.0882 | 2041.0686 | 1972.7499 | 1936.8537 | 2085.0704 | 1404.5856 | 2188.5134 | 2067.7013 | 1991.663 | 2143.3536 | 2134.476 | 2056.5078 | 1343.6006 | 584.3755 | 1172.0936 | 2023.3135 | 1937.6673 | 2137.9498 | 2115.9489 | 1408.4454 | 1533.8893 | 1682.878 | 2050.3321 | 1848.464 | 1848.464 | 1795.9705 | 1684.422 | 1610.3562 | 1158.8697
Waste cycles | 12503.378 | 6080.8559 | 2552.2471 | 2423.953 | 1779.2733 | 1495.0494 | 1185.1942 | 3324.113 | 761.3626 | 4940.9492 | 4377.2236 | 823.8467 | 1194.2609 | 953.6862 | 2530.235 | 9397.3647 | 4130.979 | 1731.73 | 1902.6097 | 955.5279 | 1012.7349 | 2780.6217 | 1074.1276 | 4759.9969 | 969.9516 | 511.5607 | 648.8355 | 748.7625 | 301.5317 | 1049.6913 | 3418.1914
Waste cost does not scale linearly to time waste. Attention to the “rms weight”/quantity of wasted cycles
60%
40%
30%
70%

## Slide 8: Transitioning from DC to PPM
1

## Slide 9: Direct versus Cycling operation
Magnet type | Total (1.2sec) | Recoverable | Thermal loss (1.2sec)
Quadrupole (26Gev) | 11kJ | 6kJ | 5kJ
Small Dipole (26Gev) | 31.5kJ | 25kJ | 6.5kJ
Large Dipole (26Gev) | 101kJ | 82kJ | 19kJ
* Assuming cost of electricity between 0.09 and 0.15CHF/kWh. 1kJ of energy over a 1.2sec cycle corresponds to 1kJ/1.2sec=0.83kW of average power. Assuming this 1.2sec (PS) cycle repeats for 24hours over 270 working days the total energy required from the power network (for each 1kJ) is 5378kWh/annum. If this energy is not recovered in capacitor banks after every magnet cycle it is returned to the power network and is not remunerated by the provider.
Annual cost of electricity for 1kJ:
(Non-recoverable/consumed every 1.2seconds)
484- 806Euro*
1
Cost 9KEur up to 15.3kEur per year*
Cost 21KEur up to 35kEur per year*

## Slide 10: Example North Area Consolidation
Action for Operators:
Employ new FGC functionality developed for transfer lines to perform:
pre-functions and post-functions such as MINRMS and
dynamic economy.
1
Action for equipment designers:
Replace solid yokes in magnets with laminated silicon steel of latest technology.
Moving complexity to software


## Slide 11: The East Area example
Chart: SUM OF output power in all circuits (excl T08)
Chart: Sum of INPUT Power (excl T08)
11
GWh/year
15
GWh/year
0.6
GWh/year
2012
<2010
2021
As built in 1967
Spectrometer removed
New cycling operation
Magnets
Solid to laminated yoke
Converters
Regenerative braking technology
1

## Slide 12: Magnetic field reproducibility
2
(c) Rey Hori / KEK

## Slide 13: The impact
Calculation for SPS mains monthly cost
August 2022, magnets only, scenario 90Eur/kWh
Physics cycles: 778,302 Euro
“degauss” cycles: 54,001 Euro
“waste” cycles: 82,320 Euro
2
Thanks to Nikos Charitonidis
See talk : Energy-efficient operation – concrete ideas to save energy
It is evident (see Nikos talk) that “de-gaussing” cycles and pre-functions are consuming “accelerator time” and energy
Preliminary data source

## Slide 14: Impact to a Consolidation Project: the SPS Octupoles case
Series connected magnets
Peak stored energy 140 Joule
Max OP current: 15A
Max required voltage 400V
Required converter ratings:
Max current: 15A
RMS current: 15A
Max voltage: 400V
RMS power: 6kW
Peak power: 6kW

## Slide 15: Impact of a magnetic reset pulse
RPPDJ.BB3.LOF
Series connected magnets
Peak stored energy 27KJoule
Max OP current: 200A
Max required voltage 1800V
Required converter ratings:
Max current: 15A 200A
RMS current: 15A 35A
Max voltage: 400V 1800V
RMS power: 6kW 63kW
Peak power: 6kW 360kW

## Slide 16: The issue non linear B=f(I)
Magnetic reproducibility issues due to:
  Magnetic field saturation
  Magnetic Hysteresis (phenomenon of energy loss in magnetic material)
  Eddy currents (magnet-end caps, vacuum chamber)
  High frequency phenomena (skin depth, proximity effect)
2

## Slide 17: Example of magnetic measurements
Field difference of 10010-4
Thanks to Carlo Petrone, TE/MSC/MM -29 05 2018
2
2

## Slide 18: From Hardware to Software solutions
Phase A: Build intelligence into FGCs
  Implementation the RMS minimiser into FGCs
  Implementation of an UP-MIN-MAX magnetic pre-function
  Software adjustable ramp rates, max value, flat-top duration
  Software implementation of the current stabilisation
  Suitable for Transfer Lines but not for Rings
Part B: Train ML models with real magnet data
  Physics-informed NN demonstrator already built!
  Start with MBI and QD/QFs in the SPS
https://indico.cern.ch/event/1019698/contributions/4279813/attachments/2212392/3744574/main.pdf
Francesco Velotti, on Hysteresis prediction on quadrupoles
2
DONE
Only a partial solution

## Slide 19: Solving the magnetic field reproducibility
With the evolution of computational tools such as machine learning, it is becoming possible to revisit the problem
Magnetic measurements Lab
Accelerator
Train Machine learning models (or PINN as proposed) with real all-inclusive data of magnetic field for a variety of Supercycle compositions
Use PINN to guess the magnet current that results in the desired field-value using as input the magnetic history
Phd Student starting on this in BE-CSS!
2
Cross-department effort.
Moving complexity to software


## Slide 20: Better to avoid saturation all together
~80% of the magnets enter saturation in transfer lines
Result of the historical beam energy increases or reuse of old magnets in new accelerators (example ISR, Linac3…).
Results to unnecessary I2R in the magnet/powering system upstream.
Tesla per Ampere ratio is very poor
Current
Voltage
Magnet Inductance
3
Inductance is half at full current!

## Slide 21: Equipment Operation, maintenance & End of life
4

## Slide 22: Situation today
Consolidation work
Initiated and driven by equipment Groups
Typically a fragmented effort, missing system level view
Off-line, not informed by machine operational data.
Preventive maintenance
Mainly comprises:
Visual inspections
Scheduled replacement of parts
Adjustments of parameters
Is mostly done off-line, not informed by machine operational data
4
Future decision-making to be informed using data analytics!

## Slide 23: SIRIUS converter fleet
BOOSTER
AD
SPS
ISOLDE
PS
EAST AREA
nToF
SIRIUS 4P+
SIRIUS 4P
SIRIUS 2P
SIRIUS S
Small quadrupoles & correctors
Small quadrupoles & dipoles
Large dipoles & series-connected magnets
Extra large dipoles & high energy beams
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
S
T11:CLOUD
T10
T9
T8:IRRAD
F16
FTN
F61
F62
F63
T08
T09
T11
BTL
FTA
4

## Slide 24: Power Converter fleet management
4
Source: https://converters.web.cern.ch/converters/converterAnalytics.php?asset=RPAFB.269.F16.RBHZ378
Athena: is a data analytics prototyping experiment.

## Slide 25: Power Converter fleet management
4
Source: https://converters.web.cern.ch/converters/converterAnalytics.php?asset=RPAFB.269.F16.RBHZ378

## Slide 26: Power Converter fleet management
4
Source: https://converters.web.cern.ch/converters/converterAnalytics.php?asset=RPAFB.269.F16.RBHZ378

## Slide 27: Power Converter fleet management
event
4
Source: https://converters.web.cern.ch/converters/converterAnalytics.php?asset=RPAFB.269.F16.RBHZ378
Moving complexity to software


## Slide 28: Exploration of new directions with ML
Prognostics of component degradation in power converters
Project objectives:
Identify signatures to be searched for
Find minimum data requirements, what, how often, what precision
Train ML models with simulated/real data
Thanks to Timm Baumann, European Power Electronics Conference 2022
4
Moving complexity to software


## Slide 29: Summary
Replacement of magnets is of paramount importance for energy efficiency
However:
We are constantly moving complexity from Hardware to software
  New FGC CClibs to minimise flux walking effect
  New prefunctions with IRMS minimiser algorith
Data science team to revisit problems with new computational tools
  Concept includes the entire Balance of System (cables, power supply, magnet, cooling)
  Interesting aspects: data sampling, field homogeneity, powering reproducibility etc…
Operation & maintenance using data analytics
New data-informed Consolidations in the future
4

## Slide 30: Ideas for the Mega-accelerators

## Slide 31: From Hardware ownership to service ownership
Mega-structures to require, virtually, infinite software services, agents, and on demand tools to be deployed for operation and development.
Some of them to only be used occasionally (data analysis, machine development, prognostic functions)
Ownership (administration, maintenance) of computing infrastructure too expensive for the “common user”.
Energy use of data-centres to be constantly scrutinised internally & externally
The State of the art solution is Containerisation & Orchestration
n-1

## Slide 32: Kubernetes
Thanks to Remi Voirin, BE-CSS more on: https://indico.cern.ch/event/1054891/
n-1

## Slide 33: From basic models to digital twins
Operator to test new machine configuration
Load profile to digital twin and verify
Minimise downtime due to misconfiguration
This technology is a consequence of our recent ability to run simulation models in real time.
Refers to a model that runs next to a physical system
Receives stimuli from physical/ production systems
Replicates the behaviour of a process or of an entire system
Aims to identify
inefficient operation
incorrect inputs or stimuli
incoherent outputs of a physical system
n

## Slide 34: From basic models to digital twins
Today, when someone asks one of these questions, at least x experts need to calculate/simulate and at least one person needs to aggregate results.
What is the expected reliability of an asset or of a process?
What is the operation cost of energy for an SFTPRO Cycle?
Which equipment consumes the largest energy in a complex?
What is the operating capacity a certain asset (substation, etc)?
What is the remaining lifetime of certain equipment/installation?
How will data analytics be done tomorrow while operating mega-structures?
#softwareAutomation #onlySolution
n

## Slide 35: Selected take away messages
Impact of higher energy consumption is multifaceted.
Environment & CERN Establish Key Performance Indices on which we can act day to day.

## Slide 36: Selected take away messages
Impact of higher energy consumption is multifaceted.
Environment & CERN Establish Key Performance Indices on which we can act day to day.
Ability to spend in new projects Use discounted cashflow methods to bring future costs to present

## Slide 37: Selected take away messages
Impact of higher energy consumption is multifaceted.
Environment & CERN Establish Key Performance Indices on which we can act day to day.
Ability to spend in new projects Use discounted cashflow methods to bring future costs to present
Planning of Mega-machines:
Effective use of computing resources
Integrate expert knowledge in digital twin accelerator models

## Slide 38: Thank you

## Slide 39: A look into the way we operate our machines
Accelerator Ring
Transfer Lines in DC
Cycling Transfer Lines
SPS
LHC
Storing energy in the magnets
Recovering energy in the magnets
Non-recoverable thermal losses

## Slide 40
Control Room
Local front-end
Surface building
Tunnel
Machine protection (WIC)
Personnel Protection (EIS)
AC Distribution
DC distribution
Heat Exchanger
Recycled energy
Thermal losses

## Slide 41: Software solution for magnetic “reset”
During this operation we always arrive at the desired field by following a downwards current path.
Point D is unique hence we will arrive at any field density with much better accuracy
Up-Min-Max Type – introduced when in transition to a higher current
2

## Slide 42: SPS user data in August 2022
Preliminary data – to be scrutinized  https://cernbox.cern.ch/s/eiamKRvTYJlFtLK
Cycles | count | beam cycles | Imax,min | Imax,max | Prms,max | Ecycle | Ephysics | Ewaste | Efficiency
3.6 | 139907 | 0 | 1531.96 | 2340.07 | 5.6 MW | 786 | 0.00 | 600.01 | 0.0%
7.2 | 18524 | 15343 | 2339.92 | 4814.68 | 28.1 MW | 1041 | 612.69 | 50.09 | 82.8%
8.4 | 1346 | 1037 | 902.59 | 5527.43 | 31.7 MW | 100 | 32.63 | 11.75 | 77.0%
10.8 | 147705 | 134108 | 894.58 | 4829.42 | 46.3 MW | 20518 | 18191.14 | 414.96 | 90.8%
24 | 619 | 435 | 5784.72 | 5784.78 | 16.3 MW | 67 | 47.21 | 19.97 | 70.3%
27.6 | 6410 | 4851 | 730.45 | 5784.8 | 14.5 MW | 713 | 527.96 | 169.49 | 75.7%