## Slide 1
Technical
Infrastructure

## Slide 2
Tue 08/11/22 16:44
Evacuation alarms in SPS 4,5,6 et ECA5. (AFT 762476)
Fire Brigade confirmed an alarm on one of the evacuation buttons in the tunnel. Since no access was given since a long time (nobody possibly present in the tunnel), the alarm was reset remotely, but the reset did not work.
SPS interlock on a kicker magnet (fire alarm) seems to be a consequence of the evacuation alarm (interlock?)
Alarm was reset locally by Fire Brigade, but the ventilation for the air extraction of the BA5 beam dump couldn't restart. This was due to a problem with a flow meter that didn't allow for the restart.
Level 3 alarm "Hydrogen leak" and evacuation of EHN1. Fire Brigade on-site, it was a false alarm caused by manipulations done by users of the experiment.
Wed 09/11/22 18:43

## Slide 3
Sun 13/11/22 01:42
Fire alarm SFDEI-56504 in SPS PA6. Evacuation BA5, BA6, BA1 triggered. (AFT 765033)
Ventilation of BA6 stopped.
On site, 10 sensors are showing elevated readings but not enough to go into alarm. No evidence of smoke.
The ventilation had a mechanical problem that caused the smoke, it was left off for the weekend and repairs will be planned as soon as possible were done, a bearing was replaced.