## Slide 1: SPS YETS22-23: Controls Activities
Vacuum Seminar, 04th April 2023
A. Gutiérrez, TE-VSC-ICM

## Slide 2: Outline:
SPS complex in the CERN accelerator complex
YETS22-23 Scope:
  Consolidation projects
  Layout modifications
  Mitigation of control system weaknesses
  De-cabling & cabling campaigns
  Commissioning and methodology
Problems
Where we are now?
Out of the SPS ring
Abel Gutiérrez – VSC seminar – April 2023

## Slide 3
SPS complex in the CERN accelerator complex
Abel Gutiérrez – VSC seminar – April 2023
North Area
AWAKE
Vacuum instrumentation in SPS | 
P [mb] | -9
Pirani | 141
Penning | 157
Full Range | 12
Ion Pumps | 1518
Sector Valves | 117
Fast Valves | 10

## Slide 4: Consolidation campaigns: Ion pump controllers
Abel Gutiérrez – VSC seminar – April 2023
Why?
To replace the existing old ion pump controllers (+30 years of operation)
By what?
New Agilent controllers (better performance and diagnostic, new features…)
How?
Coupling it with the consolidation of the ion pumps and layout modifications
LS2:
LSS2, LSS3, LSS5, Arc 5+
YETS21-22:
LSS4, Arc 4-
YETS22-23:
LSS6, Arc 6+
YETS23-24:
LSS1, Arc 1-
EYETS24-25:
Arcs 3- & 3+
LS3:
6 remaining arcs

## Slide 5: Consolidation campaigns: Ion pump controllers
Abel Gutiérrez – VSC seminar – April 2023
 | Old | Agilent | Total
BA1 | 183 | 20 | 203
BA2 | 156 | 51 | 207
BA3 | 161 | 45 | 206
BA4 | 81 | 118 | 199
BA5 | 73 | 123 | 196
BA6 | 73 | 126 | 199
Total | 727 | 483 | 1210
 | Old | Agilent | Total
BA1 | 104 | 9 | 113
BA2 | 79 | 28 | 107
BA3 | 84 | 25 | 109
BA4 | 40 | 48 | 88
BA5 | 40 | 42 | 82
BA6 | 38 | 46 | 84
Total | 385 | 198 | 583
Ion pumps in SPS; per point (2023)
Ion pump controllers in SPS; per point (2023)
LSS2
LSS3
Arc4-
LSS4
Arc5+
LSS5
LSS6
Arc6+
SPS ring: consolidated ion pumps controllers
LSS done
Arc done
~40% of the total!
~34% but 1x Agilent = 2x Old

## Slide 6: Consolidation campaigns: Ion pump controllers
Abel Gutiérrez – VSC seminar – April 2023
Analysis
What?
Where?
When?
Who?
Database
New ctrl types
PLC
HW config
Validation
SCADA test
Deployment
SCADA & PLC
Purchase
Controllers
Crates
Cables
Connectors
Profibus
Fabrication
Crates
Local Cables
Test
Controllers
Crates
Local Cables
Installation
Controllers
Crates
Local Cables
Profibus
Hardware
Software
Commissioning
Insulation tests
Communication tests
Open cable tests
Measurement tests
Interlock tests
Design
Rack layout
Interlocks
Alarms
Profibus
Process of ion pump controller consolidation

## Slide 7: Consolidation campaigns: Ion pump controllers
Abel Gutiérrez – VSC seminar – April 2023
All VPI controllers in LSS6 & Arc 6+ consolidated to Agilent
LSS6
Arc 6+
Old controller removal
New controller installation
Profibus network installation
Wiring convention modification
Old controllers removed | New controllers installed | Pumps consolidated | Connectors modified
71 | 46 | 126 | 282
Summary of ion pumps consolidated in BA6 (YETS22-23)
Notes: So here you can see some pictures of the consolidation campaign in point 6 during this last YETS, for example with the removal of the obsolete controllers and the installation of the ones, as well as the installation of the new Profibus network and the wiring convention modification of the ion pump cables. And to have a graphical idea, you can see here how all the LSS and arc 6+ was consolidate to Agilent. About the numbers, 71 controllers were removed, 46 new controllers installed, 126 ion pumps consolidated to Agilent control and 282 connectors modified, and you may wonder, why do we have to modify the connectors?

## Slide 8: Consolidation campaigns: Ion pump controllers
Abel Gutiérrez – VSC seminar – April 2023
HV
Red
Brown
VRP04
(SPS convention)
HV
Brown
Red
Internal & External
Shielding
VRP03
(SPS convention)
HV
Red
Brown
VPI003
(LHC convention)
Internal
Shielding
External
Shielding
Internal & External
Shielding
HV conductor | 1 | Pump supply & Current measurement
Brown wire | 2 | 
Red wire | 5 | Interlock loop
Internal shielding | 4 | 
External shielding | 4 | 
HV conductor | 1 | Pump supply & Current measurement
Internal shielding | 2 | 
External shielding | 2 | 
Brown wire | 4 | Interlock loop
Red wire | 5 | Interlock loop
HV conductor | 1 | Pump supply & Current measurement
External shielding | 5 | 
Internal shielding | 3 | Noise mitigation
Brown wire | 2 | Interlock loop
Red wire | 4 | Interlock loop
But…why do we have to modify the wiring in the connectors? Because in SPS we are different!
Shielding used to lower the resistance and voltage drop in the interlock circuit (relay actuation)

## Slide 9: Consolidation campaigns: Ion pump controllers
SPS type
Ion Pump
Controller
Ion
Pump
Convention:
VRP04
Abel Gutiérrez – VSC seminar – April 2023
RXVA
RXVE
Convention:
VRP03
Convention:
VRP03
Convention:
VRP03
Ion
Pump
RXVE
Convention:
VRP03
Convention:
VRP04
SPS type
Ion Pump
Controller
Ion
Pump
Convention:
VRP04
RXVA
Convention:
VRP04
Standard (old) SPS convention (1 single pump)
Standard (old) SPS convention (chain of ion pumps)
E.g.: one single ion pump in SPS
E.g.: chain of six ion pumps in SPS

## Slide 10: Consolidation campaigns: Ion pump controllers
cPS/LHC type convention applied everywhere:
Same HW for all machines (local cables & local boxes)
Easier troubleshooting (unique convention)
Easier maintenance
Much more reliability
Time consuming implementation
More manpower
Agilent
Ion Pump
Controller
Local Box 1
Local Box
2
Convention:
VPI003
Convention:
VPI003
Convention:
VPI003
Convention:
VPI003
Ion
Pump
Ion
Pump
Abel Gutiérrez – VSC seminar – April 2023
PROS
CONS
SPS type
Ion Pump
Controller
Ion
Pump
Convention:
VRP04
RXVA
RXVE
Convention:
VRP03
Convention:
VRP03
Convention:
VRP03
Ion
Pump
RXVE
Convention:
VRP03
Convention:
VRP04

## Slide 11: Consolidation campaigns: Passive gauge controllers
Abel Gutiérrez – VSC seminar – April 2023
Consolidation of old TPG 300 controllers providing interlocks:
TPG 300 controllers with +30 years of operation still installed
Some of them providing interlocks and vacuum alarms
Susceptible to failure due to electrical glitches
12x new TPG 500 controllers replaced TPG 300 providing interlocks/alarms
Running to failure as replacement strategy can be an option (if no interlock)
Smooth transition to TPG 500
TPG500 controllers in BA4 (MSE4 & sector 430)
PROBLEMS
SOLUTION

## Slide 12: Layout modifications
Abel Gutiérrez – VSC seminar – April 2023
Sector valves relocation of MKE4 sector:
VPIA_41620 & VVSB_41620 switching positions
No need of pulling new cables due to proximity of the affected equipment
Database, SCADA & PLC update, equipment reconnection, and test
MKE4 sector valve relocation

## Slide 13: Mitigation of control system weaknesses
Abel Gutiérrez – VSC seminar – April 2023
Implementation of new redundant interlocks for external alarms:
Several vacuum alarms generated during the Run 2022 due to pressure spikes (MKDVs & MKDHs)
Single source providing vacuum alarms (Penning gauge)
Specially annoying during the scrubbing run
New signals added in parallel from the ion pumps controlled by Agilent
Relay status from Agilent controller available at 1Hz
Kickers, septa, and ZS tanks (except BA1 which will be done in YETS23-24)
So far, no vacuum alarms reported during scrubbing run!
Redundant vacuum alarms to kickers system in BA5
Cabling of vacuum alarms to kickers system in BA4
PROBLEMS
SOLUTION

## Slide 14: De-cabling and cabling campaigns
Abel Gutiérrez – VSC seminar – April 2023
Two de-cabling campaigns running in parallel (BA1 & BA2):
Racks power consigned during ~6w:
  Consignation & de-consignation of power outlets and Penning cables
Limited monitoring (only sector valves and Pirani gauges):
  Risk of not identifying problems until the end
Ion pumps in critical sectors supplied locally in the tunnel (e.g.: kickers, septa):
  Requiring on-site weekly supervision specially after AUG tests
Limited time to restart the vacuum system and troubleshoot (<10 days):
  With high probability of finding damaged cables (3x damaged cables during this YETS)
Cables identified and to be removed during YETS23-24 in BA4
Summary of cabling and de-cabling in SPS

## Slide 15: Commissioning and methodology
Rack Area
Tunnel Area
IT Infrastructure
1
2
3
3 validation phases:
SCADA
Controller
SCADA
Controller
Cable
(w/simulator)
SCADA
Controller
Cable
Instrument
Commissioning criteria:
New equipment
Modified equipment:
(e.g. new cabling convention)
Critical equipment:
(e.g. sector valves, interlocks)
+120 ion pumps fully validated!
Abel Gutiérrez – VSC seminar – April 2023

## Slide 16: Problems found
Abel Gutiérrez – VSC seminar – April 2023
Spacer damaged after de-cabling campaign
Cable damaged due to radiation exposure
High-voltage conductors ripped from connectors during de-cabling campaigns

## Slide 17: Problems found
Abel Gutiérrez – VSC seminar – April 2023
Penning gauge measurement: before and after earth removal from heating collar
Ion pumps measurement: before and after the wrong convention modification
Heating collar short-circuiting cable shielding with earth

## Slide 18: Where we are now?
Abel Gutiérrez – VSC seminar – April 2023
SCADA main view of SPS
Sector valves interlock test: manually triggering the interlock sources
BIS (Beam Interlock System) test: opening/closing sector valves one by one
Vacuum alarms test (ZS, kickers, septa): manually triggering the alarm sources
Only one intervention during Hardware Commissioning period
  Water leak in LSS5- generating sparking in ion pump local box -> 20m cable replaced on the fly
Smooth scrubbing run!
Good start for the 2023 Run!
Beam Interlock System monitoring view

## Slide 19: Out of the SPS ring: AWAKE-DPS
Abel Gutiérrez – VSC seminar – April 2023
New control system:
  2x Motorized injection valves
  5x Insulation valves
  2x Full-range gauges
  2x Capacitive gauges
  2x Piezo gauges
  Software interlocks
  1x New PLC Remote IO
SCADA synoptic of AWAKE

## Slide 20: Out of the SPS ring: new BSGs in North Area
Abel Gutiérrez – VSC seminar – April 2023
SCADA synoptic of North Area
New instrumentation:
  4x Ion pumps
  4x Penning gauges
  1x Master PLC

## Slide 21
Abel Gutiérrez – VSC seminar – April 2023
Benjamin Bayliss
André Rocha
Joao Rebelo
Nicolas Levorin
Philippe Bouvard
Chiara Pasquino
Anthony Harrison
Jarmo Kortesmaa
Alban Sublet
Carolina Amoedo

## Slide 22
Abel Gutiérrez – VSC seminar – April 2023
Any
Questions?