## Slide 1: Preliminary findings from YETS 22-23 tunnel inspections.
G. Aparicio, WP15
27/01/2023

## Slide 2: Scope
Checks on equipment installation:
  Measurements of the height of the grouts of all the jacks installed in P5 Long Straight Sections Right and Left.
  Check on the installation of the vacuum control boxes (VRJA, VRTA, VRJNA..) in P5.
  Check of the overpressure protection in the UJ56.
Civil Engineering checks and findings:
  Measurements of the dimensions of the trench below the QRL all along the Long Straight Sections in P1 and P5.
  Measurements of the dimensions of the blockhouse of P5 Long Straight Sections Right and Left (in collaboration with WP8).
  Identification of the position of the manhole located in the RZ54.
  Check on the discontinuities found in the CE P5 3D models.

## Slide 3: Measurements of the height of the grouts of all the jacks installed in P5 Right and Left.
Visit report: Jack’s grout measurements: EDMS 2814507

## Slide 4: Check on the installation of the vacuum control boxes in P5 Right and Left
5R
Ongoing

## Slide 5: Check on the installation of the vacuum control boxes in P5 Right and Left
5L
Ongoing

## Slide 6: Check of the survey overpressure protection
Ongoing

## Slide 7: Civil Engineering checks and findings: measurements of the trench below the QRL (1/4)
P5 Right |  |  |  |  |  |  |  |  |  |  |  | 
Description |  | DCUM [m] To be verified with the pictures taken. | Vertical Measurement [m] |  |  |  | 3D models [m] | Horizontal Measurement [m] |  |  |  | 3D models [m]
 |  |  | 1st | 2nd | 3rd | Average |  | 1st | 2nd | 3rd | Average | 
R562 | Gutter start after DFBXB | 54.882 | - | - | - | #DIV/0! | 0.465 | - | - | - | #DIV/0! | UJ56 0.715 / R571 0.796
UJ57 | After D1 | 84.548 | 0.473 | 0.469 | 0.469 | 0.470 | 0.465 | 0.926 | 0.942 | 0.930 | 0.933 | 0.929
R571 | Between the 1 & 2 concrete shielding | 98.65 & 117.55 | 0.454 | 0.451 | 0.453 | 0.453 | 0.465 / 0.447 | 0.911 | 0.916 | 0.932 | 0.920 | 0.956 / 0.788
 | Between the 2 & 3 concrete shielding | 117.55 & 130.15 | 0.462 | 0.46 | 0.464 | 0.462 | 0.402 | 0.772 | 0.772 | 0.753 | 0.766 | 0.758
 | Just before TANAR | 140.25 | 0.461 | 0.464 | 0.464 | 0.463 | 0.400 | 0.762 | 0.778 | 0.747 | 0.762 | 0.749
 | Between the central jack in D2 | 157.9 | 0.470 | 0.482 | 0.485 | 0.479 | 0.400 | 0.751 | 0.759 | 0.739 | 0.750 | 0.717
 | After Q4 | 172.688 | 0.467 | 0.469 | 0.474 | 0.470 | 0.400 | 0.726 | 0.742 | 0.734 | 0.734 | 0.753
 | Just before Q5 | 192.072 | 0.470 | 0.747 | 0.478 | 0.565 | 0.400 | 0.736 | 0.759 | 0.773 | 0.756 | 0.742
 | After Q5 | 200.301 | 0.468 | 0.465 | 0.464 | 0.466 | 0.400 | 0.716 | 0.733 | 0.716 | 0.722 | 0.723
R572 | Q7 First jack | 261.679 | 0.428 | 0.425 | 0.420 | 0.424 | 0.400 | 0.792 | 0.803 | 0.805 | 0.800 | 0.737
5R

## Slide 8: Civil Engineering checks and findings: measurements of the trench below the QRL (2/4)
P5 Left |  |  |  |  |  |  |  |  |  |  |  | 
Description |  | DCUM [m] To be verified with the pictures taken. | Vertical Measurement [m] |  |  |  | 3D models [m] | Horizontal Measurement [m] |  |  |  | 3D models [m]
 |  |  | 1st | 2nd | 3rd | Average |  | 1st | 2nd | 3rd | Average | 
R541 | Gutter start after DFBXB | -54.882 | 0.499 | 0.493 | 0.494 | 0.495 | RZ54 0.400 / R541 0.400 | 0.774 | 0.772 | 0.768 | 0.771 | 0.738
 | After D1 | -84.548 | 0.499 | 0.492 | 0.497 | 0.496 | 0.400 | 0.761 | 0.769 | 0.759 | 0.763 | 0.687
 | Between the 1 & 2 concrete shielding | -98.65 & -117.55 | 0.497 | 0.498 | 0.497 | 0.497 | 0.400 | 0.740 | 0.739 | 0.716 | 0.732 | 0.757
UJ53 | Between the 2 & 3 concrete shielding | -117.55 & -130.15 | 0.465 | 0.467 | 0.465 | 0.466 | 0.410 | 0.765 | 0.768 | 0.784 | 0.772 | 0.682
 | Just before TANAL | -140.25 | 0.471 | 0.469 | 0.469 | 0.470 | 0.410 | 0.803 | 0.800 | 0.801 | 0.801 | 0.685
R532 | Between the central jack in D2 | -157.9 | 0.488 | 0.485 | 0.479 | 0.484 | 0.400 | 0.779 | 0.791 | 0.780 | 0.783 | 0.747
 | After Q4 | -172.688 | 0.495 | 0.498 | 0.500 | 0.498 | 0.400 | 0.761 | 0.794 | 0.780 | 0.778 | 0.781
 | Just before Q5 | -192.072 | 0.496 | 0.494 | 0.499 | 0.496 | 0.400 | 0.742 | 0.737 | 0.756 | 0.745 | 0.742
 | After Q5 | -200.301 | 0.472 | 0.474 | 0.481 | 0.476 | 0.400 | 0.676 | 0.693 | 0.698 | 0.689 | 0.774
R531 | Q7 First jack | -261.679 | 0.497 | 0.497 | 0.497 | 0.497 | 0.400 | 0.756 | 0.756 | 0.752 | 0.755 | 0.812
5L

## Slide 9: Civil Engineering checks and findings: measurements of the trench below the QRL (3/4)
P1 Right |  |  |  |  |  |  |  |  |  |  | 
Description | DCUM [m] To be verified with the pictures taken. | Vertical Measurement [m] |  |  |  | 3D models [mm] | Horizontal Measurement [m] |  |  |  | 3D models [mm]
 |  | 1st | 2nd | 3rd | Average |  | 1st | 2nd | 3rd | Average | 
Gutter start after DFBXB | 54.882 | 0.467 | 0.459 | 0.461 | 0.462 |  | 0.732 | 0.737 | 0.745 | 0.738 | 
After D1 | 84.548 | 0.467 | 0.456 | 0.453 | 0.459 |  | 0.836 | 0.845 | 0.845 | 0.842 | 
Between the 1 & 2 concrete shielding | 98.65 & 117.55 | 0.464 | 0.459 | 0.455 | 0.459 |  | 0.888 | 0.832 | 0.841 | 0.854 | 
Between the 2 & 3 concrete shielding | 117.55 & 130.15 | 0.458 | 0.452 | 0.446 | 0.452 |  | 0.826 | 0.814 | 0.829 | 0.823 | 
Just before TANAR | 140.25 | 0.462 | 0.455 | 0.449 | 0.455 |  | 0.834 | 0.833 | 0.845 | 0.837 | 
Between the central jack in D2 | 157.9 | 0.510 | 0.490 | 0.485 | 0.495 |  | 0.836 | 0.838 | 0.839 | 0.838 | 
After Q4 | 172.688 | 0.477 | 0.484 | 0.483 | 0.481 |  | 0.888 | 0.889 | 0.889 | 0.889 | 
Just before Q5 | 192.072 | 0.467 | 0.469 | 0.471 | 0.469 |  | 0.823 | 0.833 | 0.833 | 0.830 | 
After Q5 | 200.301 | 0.481 | 0.480 | 0.483 | 0.481 |  | 0.863 | 0.875 | 0.862 | 0.867 | 
Q7 First jack | 261.679 | 0.458 | 0.474 | 0.462 | 0.465 |  | 0.827 | 0.811 | 0.832 | 0.823 | 
1R
Ongoing
Ongoing

## Slide 10: Civil Engineering checks and findings: measurements of the trench below the QRL (4/4)
1L
P1 Left |  |  |  |  |  |  |  |  |  |  | 
Description | DCUM [m] To be verified with the pictures taken. | Vertical Measurement [m] |  |  |  | 3D models [mm] | Horizontal Measurement [m] |  |  |  | 3D models [mm]
 |  | 1st | 2nd | 3rd | Average |  | 1st | 2nd | 3rd | Average | 
Gutter start after DFBXB | 26600.9112 | 0.451 | 0.458 | 0.465 | 0.458 |  | 0.727 | 0.727 | 0.727 | 0.727 | 
After D1 | 26574.2112 | 0.491 | 0.481 | 0.501 | 0.491 |  | 0.886 | 0.877 | 0.886 | 0.883 | 
Between the 1 & 2 concrete shielding | 26560.2332 & 26541.3332 | 0.465 | 0.462 | 0.462 | 0.463 |  | 0.869 | 0.839 | 0.852 | 0.853 | 
Between the 2 & 3 concrete shielding | 26541.3332 & 26528.7332 | 0.463 | 0.466 | 0.468 | 0.466 |  | 0.917 | 0.893 | 0.888 | 0.899 | 
Just before TANAL | 26518.6332 | 0.489 | 0.499 | 0.484 | 0.491 |  | 0.921 | 0.895 | 0.900 | 0.905 | 
Between the central jack in D2 | 26500.9832 | 0.476 | 0.451 | 0.459 | 0.462 |  | 0.901 | 0.867 | 0.876 | 0.881 | 
After Q4 | 26486.1952 | 0.461 | 0.455 | 0.448 | 0.455 |  | 0.822 | 0.810 | 0.806 | 0.813 | 
Just before Q5 | 26466.2042 | 0.469 | 0.469 | 0.465 | 0.468 |  | 0.873 | 0.889 | 0.958 | 0.907 | 
After | 26457.9752 | 0.459 | 0.449 | 0.457 | 0.455 |  | 0.786 | 0.769 | 0.761 | 0.772 | 
Q7 First jack | 26397.5542 | 0.460 | 0.469 | 0.455 | 0.461 |  | 0.848 | 0.849 | 0.828 | 0.842 | 
Ongoing
Ongoing

## Slide 11: Measurements of the blockhouse (1/2)
LEA82424MQ: 11 CONCRETE BLOCKHOUSE - RB 54 - ST0060851_01
Nez R542 - 1503 zero sur R542 - ST0437899_01
P5 Left |  |  |  |  |  |  |  | 
Longitudinal distance from the IP wall [mm] | Vertical Measurement [mm] |  |  | 3D models [mm] | Horizontal Measurement [mm] |  |  | 3D models [mm]
 | 1st | 2nd | Average |  | 1st | 2nd | Average | 
500 | 1997.0 | - | 1997.0 |  | 2002.0 | - | 2002 | 
1650 | 2021.0 | 2022.0 | 2021.5 |  | 2001.0 | 2002.0 | 2001.5 | 
2500 | 2033.0 | 2034.0 | 2033.5 |  | 2002.0 | 2002.0 | 2002 | 
3500 | 2026.0 | 2018.0 | 2022.0 |  | 1991.0 | - | 1991 | 
4500 | 2000.0 | 2000.0 | 2000.0 |  | 1997.0 | - | 1997 | 
Ongoing
Ongoing
CMS / WP8: Ideal blockhouse - 2mx2m
5L
CE / WP15

## Slide 12: Measurements of the blockhouse (2/2)
5L
P5 Right |  |  |  |  |  |  |  | 
Longitudinal distance from the IP wall [mm] | Vertical Measurement [mm] |  |  | 3D models [mm] | Horizontal Measurement [mm] |  |  | 3D models [mm]
 | 1st | 2nd | Average |  | 1st | 2nd | Average | 
500 | 2004.0 | 1997.0 | 2000.5 |  | 2001.0 | 2001.0 | 2001 | 
1700 | 2013.0 | 2012.0 | 2012.5 |  | 2006.0 | 2005.0 | 2005.5 | 
2500 | 2008.0 | 2008.0 | 2008.0 |  | 2007.0 | 2009.0 | 2008 | 
3500 | 2001.0 | 2001.0 | 2001.0 |  | 2001.0 | 2000.0 | 2000.5 | 
4500 | 2018.0 | 2016.0 | 2017.0 |  | 2001.0 | 1997.0 | 1999 | 
Ongoing
Ongoing
R561 - 1503 Ensemble complet – ST0438580_01
CE / WP15

## Slide 13: Identification of the position of the manhole located in the RZ54
RZ54 - LHC machine
RZ54 - HL-LHC machine
RZ54
Ongoing
5L

## Slide 14: Check on the discontinuities found in the CE 3D models
UJ53
UPS – R541 – RZ54
Ongoing
5L