## Slide 1
The vacuum control system at CERN
André Rocha (andre.rocha@cern.ch)
Interlocks, Controls and Monitoring Section, Vacuum Group
TE
Technology Department

## Slide 2
Vacuum at CERN
Control System Architecture
Why accelerators need vacuum
How the vacuum control system is structured
Limitations to scalability
Conclusions
Key takeaways
Configuration Infrastructure
How we manage configuration and deploy our control system
Trends and a Possible Future Architecture
What if we had to build FCC today ?
Is there any roadblock for a larger system ?

## Slide 3
Vacuum at CERN
127 km of lines under vaccum
Pressures between and mbar
Notes: No matter the installation, you will always find that the control system is based

## Slide 4
Pressure on LHC beam lines is between and mbar
10 times less than the pressure on the moon

## Slide 5
The Beam
Notes: We can compare the beam to an F1 car that needs to accelerate through the tracks

## Slide 6
Gas Molecules

## Slide 7
Beam in Vacuum

## Slide 8
Beam Vacuum
Objective:
Reduce the interaction between the beam and residual gas molecules
Increased Beam Lifetime
Less particles lost at each turn
Increased Beam Stability
Less interference to beam dynamics
Increased Beam Luminosity
Better focused beam
Reduced Experiment Background noise
Less scattered particles

## Slide 9
Insulation Vacuum
Objective:
Thermal insulation for magnets and helium distribution
To guide the beam, 1200 8T magnets are used
Current of 12kA
Superconductivity is necessary
  0 electrical resistivity
  Reduced size of conductors
Superconductivity achieved with liquid Helium
Vacuum is used as thermal insulator for magnets and helium distribution
LHC Dipole
Notes: Any gas molecules in the magnet volume could cause unwanted heat transfer to the magnets, leading to a loss of superconductivity and subsequent damage to the magnets.

## Slide 10
Process Equipment numbers
Vacuum is achieved and monitored by over 12000 pieces of control equipment
Chart: 
| Gauges | Pumps | Valves | Controllers | PLCs
Number | 3237 | 4348 | 1688 | 2681 | 377

## Slide 11
SCADA
Servers
WinCC-OA
Technical Network
Master PLC
(S7-400 x 35)
Sector Valves
NEG + Ion Pumps
LSS Beam Gauges
( … )
VPG PLC
(S7-1200 x 220)
Pumping
Group
Penning + Pirani Gauges
LSS Gauge
Reading PLC
(ET200-SP x 18)
Arc Gauge
Reading PLC
(ET200-SP x 16)
Bypass
Valves
Cryogenic
Interlocks
LSS Insulation Vacuum Gauges
Cryogenic
Interlocks
Arc Insulation Vacuum Gauges
Arc Beam Vacuum Gauges
Profibus (mobile)
Mobile Devices
User Terminals
Profibus (fixed)
Control System Architecture
General Purpose Network
Terminal
Servers

## Slide 12
SCADA Applications
as of 2023
Notes: No matter the installation, you will always find that the control system is based

## Slide 13
Configuration settings numbers
617 632
LHC
147 315
SPS
100 783
CPS

## Slide 14
Alarms
Alarm descriptions
Alarm hierarchies
Control Parameters
Attributes required to control devices
Archiving
What to archive. Which archive settings ? Archive duration
Communication
SCADA <-> PLC <-> Device
Display
The location of equipment in synoptics
Data Sharing
What to share to other systems ?
vacDB

## Slide 15
LHC
SPS
CPS
Master DB
Machine DBs
Master Database
For each device type:
Definition of Vacuum Equipment Types
Definition of Attributes
Definition of Default Attribute values
Definition of Communication block
Definition of SCADA datapoint type
Definition of alarms produced
Machine Databases
Instantiation of equipment
Specification of equipment attributes
Specification of archiving settings
Specification of data sharing
Vacuum Databases

## Slide 16
vacCC
Master
The metadata editor
Used by SCADA developers
Definition of defaults for each eqp type

## Slide 17
vacCC
Machine
The editor for the machine databases
Allows integration of equipment in the control system by non software experts
Full traceability

## Slide 18
SCADA Configuration
PLC Code
Exporter Service
LHC
SPS
CPS
vacCC Machine Backend
MASTER
vacCC Master
vacCC Machine
Vacuum Devices
vacCC Master Backend
Configuration
Architecture
Data flow
Import
SCADA
Notes: All

## Slide 19
Advantages of Database-Driven Configuration Engineering Tools
Cross-layer consistency
  Changes of parameters are propagated to all relevant layers of the control system
Data integrity
  Configuration integrity and consistency done by defining rules for data validation and constraints
Assessibility
  Multiple people can work in the configuration of the control system at the same time
Versioning
  Have different versions of the control system ready in advance according to the needs of operations
History
  Log every change. Know what changed, when it changed and who changed what.

## Slide 20
SCADA
User Interface

## Slide 21
Automatic Synoptic Drawing

## Slide 22
Equipment Details Panel

## Slide 23
Archiving

## Slide 24
Alarms

## Slide 25
(known) factors that may eventually limit our current architecture
Source: https://www.winccoa.com/documentation/WinCCOA/3.18/en_US/Installation/Operating_Conditions.html
Maximum number of datapoint elements: ~16M
Implications on memory and CPU load
LHC: currently at 400.000
Devices and datapoint elements
Average CPU load by event manager should be < 20%
Summarized average CPU of all WinCC-OA processes (drivers, event, data, ctrl) should be < 50 %
LHC Total CPU load < 3% / Event Manager Load 10% on single core
LHC currently at 14GB/256GB memory usage
Memory and CPU
Maximum number of 512 connections per system
LHC currently with 300 connections
Number of PLC Connections
WinCC-OA Limitations to Scalability

## Slide 27
Scaling to FCC
Scaling our current architecture to an accelerator the size of FCC won’t work
  FCC planned size is roughly 4 times that of LHC
  WinCC-OA is limited to 512 PLC connections
    LHC has 300 PLCs x 4 = 1 200 PLCs – too many connections
(New) trends have to be considered for future control system architectures
  Integration of IOT devices
  Advanced real time data analytics – increasingly important on large scale systems with huge amounts of data to analyze
  Data pipelines – provide robust ways of moving large amounts of data between the different parts of the control system

## Slide 28
producer
producer
Kafka
Distributed streaming platform
Publish/subscribe messaging system based on topics
High Throughput / Low latency
  Hundreds of thousands of messages per second on a single broker
Scalable without compromising performance
  Designed to scale horizontally by adding more brokers to the cluster
  Topic partitioning – distribute data across multiple brokers
Highly available and Fault-tolerant
  Automatic Failover
  Topic replication
Ecosystem of pre-made connectors, allowing to integrate kafka with a multitude of systems
  https://docs.confluent.io/kafka-connectors/self-managed/kafka_connectors.html#kafka-connectors
Kafka broker
Kafka broker
Kafka broker
producer
producer
producer
producer
producer
producer
producer
producer
producer
consumer
producer
producer
consumer
producer
producer
consumer

## Slide 29
SCADA
Servers
Technical Network
User Terminals
Control System Architecture
General Purpose Network
Zone 1
Kafka Translators
Zone 1
Zone 2
Zone n
Kafka Translators
Zone 2
Kafka Translators
Zone n
Real Time Analytics
Processors

## Slide 30
Conclusion
Database-driven Configuration Engineering tools are essential to manage large-scale control systems:
  Provide a centralized location for storing and managing equipment configurations, making it easier to maintain and update control systems
  Allow for more efficient collaboration between multiple teams working on different aspects of a control system
  Improve the reliability and safety of control systems by ensuring that equipment configurations are consistent and correctly applied in the relevant layers
  Allows operators to track and monitor changes made to control system parameters, providing a clear audit trail of modifications
Distributed streaming technologies can help us evolve our control system architecture:
  Provide greater scalability, enabling control systems to handle larger and more complex deployments
  Enable real-time analytics, allowing for more proactive and predictive maintenance strategies
  Open up new possibilities for integrating different types of equipment and technologies, improving interoperability and reducing vendor lock-in

## Slide 31
Thank you !