## Slide 1
Engineering workflow in vacuum
André Rocha (andre.rocha@cern.ch)
Interlocks, Controls and Monitoring Section, Vacuum Group
TE
Technology Department

## Slide 2
Vacuum Control System
Vacuum Framework
Architecture and some numbers
Databases and Configuration Components
Configuration Workflow
Conclusions
Key takeaways
From P&ID to a production control system

## Slide 3
Vacuum at CERN
127 km of lines under vaccum
Pressures between and mbar
Notes: No matter the installation, you will always find that the control system is based

## Slide 4
Process Equipment numbers
Vacuum is achieved and monitored by over 12000 pieces of control equipment
Chart: 
| Gauges | Pumps | Valves | Controllers | PLCs
Number | 3237 | 4348 | 1688 | 2681 | 377

## Slide 5
SCADA
Servers
WinCC-OA
Technical Network
Master PLC
(S7-400 x 35)
Sector Valves
NEG + Ion Pumps
LSS Beam Gauges
( … )
VPG PLC
(S7-1200 x 220)
Pumping
Group
Penning + Pirani Gauges
LSS Gauge
Reading PLC
(ET200-SP x 18)
Arc Gauge
Reading PLC
(ET200-SP x 16)
Bypass
Valves
Cryogenic
Interlocks
LSS Insulation Vacuum Gauges
Cryogenic
Interlocks
Arc Insulation Vacuum Gauges
Arc Beam Vacuum Gauges
Profibus (mobile)
Mobile Devices
User Terminals
Profibus (fixed)
Control System Architecture
General Purpose Network
Terminal
Servers
credits R. Ferreira

## Slide 6
SCADA Applications
as of 2023
Notes: No matter the installation, you will always find that the control system is based

## Slide 7: Vacuum Framework
Developed at TE-VSC-ICM since late 1990s
Used in the largest machines (LHC, SPS, CPS, Deceleration)
WinCC-OA SCADA / Siemens PLC framework
Components:
  vacDB – set of ORACLE databases
  Vacuum Controls Configurator – vacCC
  Vacuum SCADA
  Vacuum PLC baseline
Database-driven Configuration Engineering approach
vacCC
vacDB
vacSCADA
vacPLC
Vacuum Framework

## Slide 8
Control Type
Equipment Instance
SCADA
Widget
Faceplate
Commands
Alarms
SMS Notifications
PLC code
DP Type
Archive
instanceOf

## Slide 9
Configuration settings numbers
617 632
LHC
147 315
SPS
100 783
CPS

## Slide 10
Alarms
Alarm descriptions
Alarm hierarchies
Control Parameters
Attributes required to control devices
Archiving
What to archive. Which archive settings ? Archive duration
Communication
SCADA <-> PLC <-> Device
Display
The location of equipment in synoptics
Data Sharing
What to share to other systems ?
vacDB

## Slide 11
LHC
SPS
CPS
Master DB
Machine DBs
Master Database
For each control type:
Definition of Attributes
Definition of Default Attribute values
Definition of Communication block
Definition of SCADA datapoint type
Definition of alarms produced
Machine Databases
Instantiation of equipment:
Specification of equipment attributes
Specification of archiving settings
Specification of data sharing
Vacuum Databases
Definition of Control Types
Instantiation of equipment

## Slide 12
vacCC
Master
Used by SCADA developers
Definition of control types, their attributes, and default values

## Slide 13
vacCC
Machine
The editor for the machine databases
Allows integration of equipment in the control system by non software experts
Full traceability

## Slide 14
P&ID approved
Naming Conventions Applied to P&ID
Create/Update machine in vacCC
Configuration
Export
ECR – Engineering Change Request
Typical requests:
  New machines
  New vacuum lines
  New sectorization
Vacuum controls equipment upgrades
Configuration Workflow
P&ID
SCADA Configuration
PLC Code
vacCC Machine
Deploy test SCADA application and PLC code
Commissioning
Deploy prod SCADA application and PLC code
Production
Test Environment

## Slide 15
SCADA Configuration
PLC Code
Exporter Service
LHC
SPS
CPS
vacCC Machine Backend
MASTER
vacCC Master
vacCC Machine
Vacuum Devices
vacCC Master Backend
Configuration
Architecture
Data flow
Import
SCADA
Synchronizer
Service
Layout
PLC Baseline
Notes: All

## Slide 16
SCADA
User Interface

## Slide 17
Automatic Synoptic Drawing

## Slide 18
Equipment Details Panel

## Slide 19
Archiving

## Slide 20
Alarms

## Slide 21
Advantages of Database-Driven Configuration Engineering Tools
Object oriented-like paradigm
  Each equipment instance inherits a default configuration, but the user is free to override configuration
Cross-layer consistency
  Changes of parameters are propagated to all relevant layers of the control system
Data integrity
  Configuration integrity and consistency done by defining rules for data validation and constraints
Assessibility
  Multiple people can work in the configuration of the control system at the same time
Versioning
  Have different versions of the control system ready in advance according to the needs of operations
History
  Log every change. Know what changed, when it changed and who changed what.

## Slide 22
Conclusion
The vacuum configuration workflow is streamlined through the Vacuum Controls Configurator infrastructure:
  Updates to individual equipment and machines are done through vacCC Machine
  Default values are managed through vacCC Master
Database-driven Configuration Engineering tools are essential for the management of large-scale control systems
Future Work
Automate SCADA deployment
  Objective: minimize human intervention by automating SCADA deployments
  Instead of generating configuration files and updating the SCADA manually, generate a new container image of the SCADA application
  Deploy to development and production environments with the push of a button
Automate PLC projects build
  More on this by R. Ferreira