## Slide 1: Cryogenic Cooling and the Physics of Superfluid Helium
Andrea Vitrano
Machine Protection and Electrical Integrity Group (TE-MPE-PE)
24th August 2023 – PE Section Meeting
cern.ch/steam

## Slide 2
Outline
Cryogenics
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC main dipole
Recent He II Studies
Conclusions
1
2
3
4
5
6

## Slide 3
Cryogenics
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Van Sciver, S.W., 2012. Springer New York.

## Slide 4
Cooling below 120 K
Coolant type: cryogens
Baudouy, B., 2015. arXiv:1501.07153.
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions

## Slide 5
Cooling below 120 K
Coolant type: cryogens
Material properties: contraction, embrittlement, etc..
Baudouy, B., 2015. arXiv:1501.07153.
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
T (K)
L = 27 km
dL = 81 m !

## Slide 6
Cooling below 120 K
Coolant type: cryogens
Material properties: contraction, embrittlement, etc..
Equipment: insulated systems, measuring devices
Cernox® CX
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions

## Slide 7
Cooling below 120 K
Coolant type: cryogens
Material properties: contraction, embrittlement, etc..
Equipment: insulated systems, measuring devices
Consumption: energy-intensive processes
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Carnot Factor
Wagner, U., 2004. CAS

## Slide 8
Cooling below 120 K
Coolant type: cryogens
Material properties: contraction, embrittlement, etc..
Equipment: insulated systems, measuring devices
Consumption: energy-intensive processes
Safety: personnel and environmental hazards
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Koettig, T., 2014. (No. CERN-HSE-PHO-2014-007).
Frostbites
Asphyxiation
Flammable gas
Oxidizing gas
Gas/liquid volume ratio: ~ 700-800 !
Pressure build-up

## Slide 9
Cryogenic cooling
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Baudouy, B., 2015. arXiv:1501.07153.
System subjected to:
Thermal radiation (outer vessel)
Conduction (current leads, structural supports)
Internal dissipation (AC losses, Joule effect)
Maintain Tsystem ~ constant:
Shield incoming heat loads
Extract internal heat loads
T∞

## Slide 10
Heat transfer regimes
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Murshed, S., 2016. DOI: 10.5772/63321
Singh, S.K., 2021. DOI: 10.1016/j.ijheatmasstransfer.2021.122020
Flow boiling

## Slide 11
Cryogenic cooling
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Baudouy, B., 2015. arXiv:1501.07153.
Direct cooling:
Cryogen in direct contact
Large heat transfer rate
Uniform temperature
Indirect cooling:
No direct contact with cryogen (a)
Dry systems (b)
Moderate heat loads
(a)
(b)

## Slide 12
Forced flow
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Baudouy, B., 2015. arXiv:1501.07153.
Advantages:
Reduced amount of cryogen
Adjustable heat transfer rate
Nearly constant temperature (TP)
Higher heat transfer coeff (SC, TP)
Disadvantages:
Circulation system
Pressurization system (SC)
Sub-cooling system (SP)
Orientation matters (TP)
Indirect
Direct
SP: single-phase
TP: two-phase
SC: supercritical

## Slide 13
Circulation loops
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Baudouy, B., 2015. arXiv:1501.07153.
Advantages:
No pumping system
Auto-tuned mass flow
Higher heat transfer (TP)
Disadvantages:
Gravity dependent
Flow instabilities
Mixed convection
(Ri = Gr / Re2)
SP: single-phase
TP: two-phase

## Slide 14
Bath cooling
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Baudouy, B., 2015. arXiv:1501.07153.
Advantages:
No mass flow
High heat transfer (SB)
Nearly constant temperature (SB)
Disadvantages:
Large amount of cryogen
Limited temperature range
Risk of film boiling (SB)
Risk of leaks (SB)
Limited heat transfer (PB)
Temperature stratification (PB)
SB: saturated
PB: pressurized
Superfluid Helium

## Slide 15
Helium (4He)
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
No triple point
Solid under external p only
Lambda point:
Tλ = 2.17 K
pλ = 5.04 kPa
at atmospheric pressure:
Tλ = 2.168 K
Tsat = 4.2 K
4He phase diagram

## Slide 16
Two-fluid model
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Two-fluid model:
Entropy: ss = 0, ρnsn = ρs
Viscosity: µs = 0, µn = µ
v = 0  counterflow:
Liquid helium density
T λ

## Slide 17
Thermo-mechanical effect
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Fountain effect:
London’s eq:
Mechano-caloric effect
Rollin film:
Van der Waals forces
Frictionless film
Heat flow in film
Van Sciver, S.W., 2012. Springer New York.
BBC

## Slide 18
Landau and Gorter-Mellink regimes
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Landau regime:
Frictionless superfluid
Critical velocity
Gorter-Mellink regime:
Quantum turbulence
Mutual friction force
He II heat transport:
1.95
Heat conductivity function
Landau regime
G.-M. regime
n ~ 3
at q = 10 kW/m2 100 kW/m K !

## Slide 19
Helium phase transitions
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Specific heat capacity
λ-point
Critical heat flux in channels:
Minimum value for λ-transition:
Peak nucleate boiling << qmin
Ehrenfest classification of phase transitions:
Derivatives of the Gibbs free energy
First-order  discontinuous entropy
Second-order  discontinuous cp
Van Sciver, S.W., 2012. Springer New York.

## Slide 20
Thermal boundary resistance
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Van Sciver, S.W., 2012. Springer New York.
Kapitza resistance:
Temperature jump
Khalatnikov theory:
Phonon transmission mismatch
Empirical formulae:

## Slide 21
LHC main dipole cooling
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
L. Evans. 2012. Philosophical Transactions of the Royal Society A
Superconducting coil
Heat exchanger pipe in saturated He II
Beam pipe
Steel collars
Pressurized He II
Cross section
P. Lebrun, L. Tavian. 2014. CAS

## Slide 22
Cooling process obstacles
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
L. Evans. 2012. Philosophical Transactions of the Royal Society A
Steel collars
M. Wilson. 2015. Joint Universities Accelerator School
200 micron thick spacing
P.P. Granieri. 2013. Cryogenics
10 micron thick spacing
Conductor
Insulating tape

## Slide 23
Recent heat and mass transfer studies
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
How does He II behave during phase transitions in confined geometries?
How to simulate it via numerical modeling?
Research work:
Experimental: test campaigns in He II cryostat in high-aspect ratio channels
Analytical: dimensional study and generalization of the He II equations
Numerical: CFD modelling of He II and its phase transitions with OpenFOAM

## Slide 24
Experimental rig and operations
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Claudet-type cryostat:
Double bath system
Pressurized He II
Pressure-regulated temperature
Helium phase diagram

## Slide 25
Insert and channel setup
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
0.2-0.5 mm thick
14 cm long
5 cm wide

## Slide 26
Clamped flux tests
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Constant heat flux applied since time 0
Fixed bath temperature
Measurements at the sensors’ location: TS1 (close to heater)  TS8 (close to bath)
Temperature difference with respect to the bath (1.8 K)
0.2 mm thick channel
horizontal orientation
q = 22.5 kW/m2
g
q
TS1
TS8

## Slide 27
Temperature evolution above qc
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Temperature evolutions at Tb = 1.9 K for different heat fluxes in the horizontal 0.2 mm thick channel

## Slide 28
Double-front propagation
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
at TS1 in the 0.2 mm thick channel
at TS1 in the 0.5 mm thick channel
Confinement number:
Threshold: Co = 0.5

## Slide 29
Hall-Vinen–Bekharevich–Khalatnikov equations
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Incompressible He II Navier-Stokes equations in the Gorter-Mellink regime
inertial forces
viscous forces
thermo-mechanical force
pressure drop
diffusive term
mutual friction force
Kitamura’s single fluid model assumption:
T. Kitamura. 1997. Cryogenics

## Slide 30
HVBK equations dimensional study
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
A. Vitrano. 2023. Cryogenics

## Slide 31
Second-order transition problem
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
A. Vitrano. 2022. Computer Physics Communications
Representation of two non-uniform adjacent control volumes
Correction algorithm:
Identify front location:
Correct face temperature:
Re-compute temperature gradient
Correct He II fields

## Slide 32
He II numerical modelling
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
A. Vitrano. 2022. Computer Physics Communications
g
q
TS1
TS8
Y. S. Ng. 1989. Journal of Thermophysics and Heat Transfer
L. Bottura. 1999. International Journal for Numerical Methods in Fluids
R. Srinivasan and A. Hofmann. 1985. Cryogenics

## Slide 33
Phase transitions numerical modelling
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
A. Vitrano. 2022. Computer Physics Communications
g
q
TS1
TS8
Tb = 2.15 K
Theater = 22.7 K

## Slide 34
Conclusions
Cryogenics
1
2
3
4
5
6
Cooling Techniques
Superfluid Helium (He II)
Cooling the LHC MB
Recent He II Studies
Conclusions
Superfluid helium: difficult to model and handle, costly to maintain, but it ensures:
High contact surface (very low viscosity)
Great thermal stability (very high specific heat)
Great heat transfer capabilities (very high effective thermal conductivity)
 Effective cooling (two-phase forced flow & subcooled bath)

## Slide 35: Thank you for your attention Questions?
cern.ch/steam
steam-team@cern.ch