| Technical Infrastructure (TI) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Facility Coordinator last week |  |  |  | Clément Pruneaux |  |  |  |  |  |
| Facility Coordinator this week |  |  |  | Jesper Nielsen |  |  |  |  |  |
| Statistics |  |  |  |  |  |  |  |  |  |
| Alarms |  |  |  |  |  |  |  |  |  |
| Phone calls |  |  | Incoming |  |  |  | Outgoing |  |  |
| ODMs |  |  |  |  |  |  |  |  |  |
| Facility Status |  |  |  |  |  |  |  |  |  |
| Summary | Another busy week in TI with quite a few events and interventions. Good coordination between the teams in CCC for several interventions requiring coordination between the islands resulted in very efficient interventions. |  |  |  |  |  |  |  |  |
| Issues | Tue 25/04/23 04:47: Electrical perturbation with a voltage dip of -27% for 55ms seen CERN wide. EDF/RTE confirmed the perturbation on the 400 kV line Génissiat / Bois Tollot. Tue 25/04/23 09:12: Electrical problem with 220V auxiliary supply for CRYO compressor in LHC8. When switched on, the fault was seen on the power supply supply further up the line, and caused a cut of the supply EMD407/8E (18kV supply for CRYO). All was back in service rapidly. Tue 25/04/23 09:38: During a maintenance on the surface ventilation in BA6, that required some welding, the smoke was seen by the fire detection system and caused the evacuation of the zone. Tue 25/04/23 19:54: During a "cleaning flush" of the BA6 demineralized water circuit the circuit was stopped and caused a stop of the SPS. |  |  |  |  |  |  |  |  |
| Plans |  |  |  |  |  |  |  |  |  |
| Intervention Request |  |  |  |  |  |  |  |  |  |
| Yes / No | Duration |  |  |  |  | Preferred date/time |  |  |  |
| Reason |  |  |  |  |  |  |  |  |  |
| Impact |  |  |  |  |  |  |  |  |  |