| Linac 4 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Machine Coordinator last week |  |  | A. Topaloudis |  |  |
| Machine Coordinator this week |  |  | J.B. Lallement |  |  |
| Statistics |  |  |  |  |  |
| Availability | 90.1% |  |  |  |  |
| Facility Status |  |  |  |  |  |
| Summary | This week has been a busy week. Several issues occurred during the week and some of them for the first time (e.g. MTG issue on Tuesday, PIMS0708 issue on Tuesday night and Friday night). PIMS0708 particularly was difficult to diagnose because of the complexity of the system and the various stake holders. |  |  |  |  |
| Issues | Tuesday morning: - Master Timing Generator (MTG) issue. Caused an issue to several RF equipment (POPSB, DTL1, CCDTL1-2, Chopper, CCDTL7) that had to be reset. (~1h) - Intervention for changing an electronic card to avoid similar issues in the future (~25mins) Tuesday night: - PIMS0708 system tripped due to a klystron interlock. The origin was complicated to identify as all klystron hardware seemed to work correctly. The interlock came from the fast interlock card due to the focus power supply bit. Once the problem was understood, the klystron piquet team called the equipment specialist and exchanged the concerned comparator card and re-adjusted the interlock threshold. The issue was solved around 4 am with the help of 5 people from RF (3 on piquet + 2 specialists) (~6h 40mins). - The restart of the high voltage was complicated because the modulator lost the reference voltage and could not be set remotely. The EPC piquet set the voltage locally and the system could be restarted around 6:40. The issue is understood, and it will be permanently solved during the IST in November (~3h). - Around 7:50 the modulator-klystron system stopped again. Equipment specialists from EPC and RF used the opportunity to stop and cleanly restart modulator and klystron. From the restart around 8:30 the PIMS0708 was back in normal condition (~50mins) Wednesday afternoon (~1h 20min): - Issue with the Chopper. Piquet had to replace the amplifier of module 2P Thursday morning: - Electrical glitch required several equipment (source, RF, power converters…) to be reset before beam was back (~40mins). Friday night: - PIMS0708 system tripped again. Similar fault as Tuesday/Wednesday. HL klystron piquet solved the issue by replacing a faulty comparator card for the focus power supply fast interlock |  |  |  |  |
| Plans | Regular operation |  |  |  |  |
| Intervention Request |  |  |  |  |  |
| Yes / No | Duration |  |  | Preferred date/time |  |
| Reason |  |  |  |  |  |
| Impact |  |  |  |  |  |