| SPS |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Machine Coordinator last week |  |  |  |  | Francesco M. Velotti |  |  |  |  |  |
| Machine Coordinator this week |  |  |  |  | Michael Schenk |  |  |  |  |  |
| Beam Scheduled |  |  |  |  |  |  |  |  |  |  |
| LHC | Yes |  | NA |  | Yes |  | AWAKE | Yes | HiRadMat | No |
| Beam Availability by Destination (AFT) |  |  |  |  |  |  |  |  |  |  |
| LHC | 96.7% |  | NA |  | 76.3% |  | AWAKE | 96.5% | HiRadMat | - |
| Facility Status |  |  |  |  |  |  |  |  |  |  |
| Summary | - Week dedicated to NA ion physics, AWAKE and LHC ion run - Ion parallel MD on Monday dedicated to LHC ion beams - Long flat top LHC cycle (5 s at 400 GeV) re-checked for the dedicated MD of Wednesday W43 – INDIV bunch injected and ramped to flat top after cycle re-mapped into operational timing users - Beam stopped to NA at 22:31 on Saturday evening following a fire on the MSN10 wobbling magnet of T2 - Dedicated AWAKE run after interruption on NA physics |  |  |  |  |  |  |  |  |  |
| Issues | - Stop of about 1h due to issue in timing card - needed about 30 min for repair - Recurrent problem (over 2 days) on RF cavities affected beam quality to AWAKE, and prevent acceleration of SFTION beam - Problem on FMCM intermittently appearing on MSE.4. First assessed that the PC was OK. Then investigation on MPE side. Finally tried to replace FMCM PS, no change and finally the card itself and problem solved - TCC8 water infiltration flooding the elevator in TCC8. - There is a blockage that prevents water from draining to the surface, which then flows into the lift pit below, via the shaft cable trays – about 4kL of water found. - This caused the loss of the patrol as well as some damages to the lift machinery and access system. Company on situ to identify the blockage. - Installed a pump in the pit to avoid future flooding. Constant monitoring needed. Zone now in restricted access and still needs RP to give access - Saturday night at around 10:30 beam interlocked by the SIS ventilation check fire in BA80 on MSN10 just after T2 (wobbling magnet) - most likely due to overheating following a water leak (which was also found on this magnet) - still not clear though why the thermo-switch that is installed on this magnet did not stop it and prevent the fire - Fire brigade evacuated EHN1 too (experiments areas) and access was given back after filters analysis on Sunday - RP analysed the filters and did not find any significant activation, so access was given back to EHN1. |  |  |  |  |  |  |  |  |  |
| Plans | - Follow up the MSN10 issue and agree on strategy for replacement and run continuation - Ion parallel MD on Tuesday afternoon – to be seen if it can be extended - Dedicated proton LHC MD on Wednesday with very high intensity for WS stress test |  |  |  |  |  |  |  |  |  |
| Intervention Request |  |  |  |  |  |  |  |  |  |  |
| Yes / No |  | Duration |  | No |  | Preferred date/time |  |  |  |  |
| Reason |  |  |  |  |  |  |  |  |  |  |
| Impact |  |  |  |  |  |  |  |  |  |  |