## Slide 1: ENERGY SAVING: PLANS & ACHIEVEMENTS Analysis of the energy consumption in CERN Sites & Future Perspectives
Michela LAGIOIA Guillaume ROUGE
30/05/2023
SCE-SAM-IN: HVAC, Sanitary and Electricity
SCE – Site and Civil Engineering
Notes: Energy savings plan and achievements

## Slide 2: SCE-SAM-IN
The Infrastructure Section (IN), within the Site Asset Management (SAM) Group in the Site and Civil Engineering (SCE) Department, is in charge of the operation, maintenance, design, tendering and work phases of HVAC, Electrical and Sanitary installations for buildings in the CERN sites.
SITE AND CIVIL ENGINEERING DEPARTMENT
Infrastructure
[SAM-IN]
SL: Christophe Martel
DSL: Guillaume Rouge
Site Asset Management
[SAM group]
GL: Pierre Cardon
DGL: Michael Poehler
Electrical works
Team referee: Fabien Vincent
Antoine Degeneve
Patrice Sajous
Oeyvind Vangen
HVAC and sanitary works
Team referee: Guillaume Rouge
Thierry Duverger
Morgan Farre
Juan Gomez
Michela Lagioia
Denis Potard
Maintenance and Methods
Team referee:
Christophe Martel
Gabriel Genamy
Franck Moro
Yoann Obry
Delphine Viallet
Admin support
Christine Alliod
+ support of Temps and Contractors

## Slide 3
Summary
3
PLAN
ACHIEVEMENT
FUTURE PERSPECTIVES
Introduction
Conclusion
Solutions proposed in 2022: application in winter season 22-23
Led installation
Shutdown of public lights at nights
No electrical radiators
Optimization of the heating district
User awareness: good behaviour – HSE Campaign
Focus on electricity consumption
Focus on gas consumption
Sustainable heating plants
Cooling strategy

## Slide 4
Total annual electricity consumption at CERN:
990’895 MWh/year
[EN-EL Energy database]
Chart: Annual gas consumption at CERN
| Heating Meyrin | Heating Prevessin
 | 50284 | 11853
Chart: Annual electricity consumption at CERN
| CERN Machines | Meyrin Buildings | Prevessin Buildings
 | 990895 | 30811 | 17873
INTRODUCTION
Energy consumption at CERN in 2021
ELECTRICITY
GAS
95 %
2 %
3 %
Total annual gas consumption at CERN:
68’971.73 MWh/year
[SCE-SAM Gas invoices]
19 %
81 %
30’811 MWh/year
17’873 MWh/year
13’156.86 MWh/year
55’814.86 MWh/year
Tertiary Buildings (5%)
Impact per person (6500 users) = 7,5 MWh/year
Tertiary Buildings (100%)
Notes: UPDATE WITH 2022

## Slide 5
Solutions proposed in September 2022
ELEC | HVAC & SAN | BEHAVIOUR | STRATEGY | MID/LONG-TERM
Led installation Public lighting No electrical radiators | Heating district Specific installations Washing hands | Communication with users | A/C for comfort | Smart working Old Barracks Renewable energy
IMMEDIATE SOLUTIONS
5
MID/LONG-TERM
PLAN

## Slide 6
Chart: EXPECTED ENERGY SAVINGS: LEDs INSTALLATION IN THE 1st YEAR [MWh/year]
| Energy saved per year | 2021 Elec. consumption in Meyrin and Prevessin Buildings
 | 845 | 48684
S1: LEDs INSTALLATION
Replacing immediately obsolete halogen lamps with LEDs reduces lighting electricity requirements by up to 65%.
Process ongoing, but far from being completed!
EXPECTATIONS: about 14’700 Led Tubes to be changed every year. Complete replacement at CERN to be completed in 8 years.
PROPOSAL: Increase in human resources to speed up the process, and to observe much more effectively the consequences of this replacement in all the buildings at CERN.
Energy involved | [Type] | Electricity
Investment costs | [CHF] | 280’000
Objective of reduction | [MWh/year] | 845
Energy savings costs | [CHF/year] | 46’000
Payback | [Years] | 6
Human resources | FTE | 2
Schedule | January 2023 | 
Scale of application | 12% of total LED number in Meyrin and Prevessin | 
Impact on Users | None | 
SAVINGS:
1,74%
Electricity
N.B. The savings represent 0,09% of CERN’s Total Electricity consumption
[990’895 MWh/year]
PLAN
Notes: Reduce text

## Slide 7
Chart: EXPECTED ENERGY SAVINGS: PUBLIC LIGHTING SHUTDOWN AT NIGHT [MWh/year]
| 2021 Elec. consumption in Meyrin and Prevessin Buildings | Energy saved per year
 | 48684 | 262.8
S2: PUBLIC LIGHTING SHUTDOWN
Many cities are currently shutting down the public lighting during the night, with the aim to save electricity while reducing CO2 emissions and night-time pollution.
The target would be to shut down public lighting during non-operational hours, Specifically, the proposal is to shut it down from 11 p.m. to 5 a.m. in both Meryin and Prevessin sites.
Energy involved | [Type] | Electricity
Investment costs | [CHF] | 2’000
Objective of reduction | [MWh/year] | 260
Energy savings costs | [CHF/year] | 14’000
Payback | [years] | 0,14
Human resources | FTE | 0,04
Schedule | November 2022 | 
Scale of application | CERN Site | 
Impact on Users | None | 
SAVINGS:
0,54%
7
Electricity
N.B. The savings represent 0,03% of CERN’s Total Electricity consumption [990’895 MWh/year]
PLAN

## Slide 8
Chart: EXPECTED ENERGY SAVINGS: RADIATORS [MWh/year]
| Energy saved per year | 2021 Elec. consumption in Meyrin and Prevessin Buildings
 | 62.16 | 48684
S3: REMOVE MOBILE ELECTRICAL RADIATORS
FROM CERN STORES CATALOGUE
On CERN Catalogue, there is the possibility for USERs to order independently mobile electrical radiators, as shown in the picture below. The proposal is to remove them from the catalogue in order to avoid the purchase of electricity consuming machines and to avoid their supply for comfort reasons.
An average of 50 units is sold every year from CERN Store.
CERN Stores Catalogue (19.09.60.E)
Energy involved | [Type] | Electricity
Investment costs | [CHF] | 0
Objective of reduction | [MWh/year] | 60
Energy savings costs | [CHF/year] | 3’400
Payback | [years] | 0
Human resources | FTE | 0,01
Schedule | October 2023 | 
Scale of application | Meyrin and Prevessin | 
Impact on Users | Moderate | 
SAVINGS:
0,13%
Electricity
N.B. The savings represent 0,01% of CERN’s Total Electricity consumption [990’895 MWh/year]
PLAN
No-more available

## Slide 9
BACKGROUND: OPTIMIZATION OF THE HEATING DISTRICT
Refurbishment of the heating plant in Meyrin & CERN’s Heating network
Leaks detection and repair in the distribution network;
Consolidation of heating substations
TG-CONS – Technical consolidations of the galleries
PLAN
Installation of new boilers and new automation
Delivered in 2019
Delivered in 2022
GAS
Delivered in 2017
Notes: 100 heating substations
75 technical galleries
Pre-requisite for future optimization
(new automation system with PLC connected to network monitoring)

## Slide 10
S4: OPTIMIZATION OF THE HEATING DISTRICT
Decrease of the Temperature in the district and delay the start of the heating
The decrease of temperature in the heating district represents another possible solution to save energy: the proposal is to reduce the temperature at the delivery point of the boiler. Moreover, the starting day of the heating district is generally scheduled for the 1st of October: this date could be adjusted depending on the needs, according to the external temperature reached. In the estimation below, it has been considered a delay of 5 days.
PROPOSAL |  | -1°C IN THE DISTRICT | 5 DAYS DELAY
Energy involved | [Type] | GAS | GAS
Investment costs | [CHF] | 0 | 0
Objective of reduction | [MWh/year] | 930 | 750
Energy savings costs | [CHF/year] | 70’000 | 56’000
Human resources | FTE | 0 | 0
Schedule | October 2023 |  | 
Scale of application | Meyrin and Prevessin |  | 
Impact on Users | None |  | 
GAS
Chart: EXPECTED ENERGY SAVINGS: HEATING DISTRICT OPTIMIZATION
| GAS Consumption 2021 | Energy saved per year (-1°C) | Energy saved per year (5 days delay)
 | 62137 | 930 | 960
1,5%
1,21%
PLAN

## Slide 11
OPTIMIZATION OF THE HEATING DISTRICT: Winter 22-23
GAS
PLAN
Where?
Tertiary Buildings** in Meyrin and Prevessin
OPTIMIZATION OF THE HEATING CURVES:
Departure temperature based on the external temperature, to consider the influence of the climate and to avoid the waste of resources.
ECO-MODE
Additional adjustment provided to the setpoint during nighttime, during the weekend, and during holidays.
** In the following years the same optimization will be applied to the Machine Buildings
SUBSTATIONS
11
Notes: 100 heating substations
75 technical galleries
Dep temperature of secondary district after the heat exchanger for every building

## Slide 12
OPTIMIZATION OF THE HEATING DISTRICT: Winter 22-23
GAS
HEATING PLANTS
PLAN
TEMPERATURE
PRESSURE
Gradually decreased along the winter season in Meyrin:
November 2022: 10 bars
April 2023: 4 bars
Meyrin:
Optimization of the departure temperature from the boiler, which is also based on the air external temperature;
The number of boilers working simultaneously changes depending on the temperature range & power needs.
Prevessin:
The departure temperature from the boiler is fixed, and it does not vary according to the external temperature. Nevertheless, it has been optimized.
Notes: Old boiler needed high pressure.

## Slide 13
S9: GOOD BEHAVIOURS – MEMO BY HSE
Communication with users is crucial to raise awareness about the energy consumption strategy. Reminders from HSE about sensitive topics are essential to warn users about their impact on energy consumption and to guide them into changing their habits at CERN.
Switch off lights when you leave the room (office, labs, corridors and halls);
Turn off computers & screens when possible;
Remember to close windows and doors, especially when heating or air conditioning is on;
Reduce the valve of radiators when possible
Avoid using domestic hot water;
Reduce/Remove air conditioning when possible.
Close blinders during summer
Energy involved | [Type] | Electricity | Gas
Investment costs | [CHF] | 0 | 0
Objective of reduction | [MWh/year] | 2’400 | 3’100
Energy savings costs | [CHF/year] | 130’000 | 230’000
Payback | [years] | 0 | 
Human Resources | FTE | 0 | 
Schedule | October 2023 |  | 
Scale of application | Meyrin and Prevessin |  | 
Impact on Users | Best effort |  | 
Chart: 
| Energy saved per year | GAS CONSUMPTION 2021
 | 3106.85 | 62137
EXPECTED ENERGY SAVINGS – GOOD BEHAVIOURS
Chart: 
| Energy saved per year | Electricity consumption in 2021
 | 2134.2 | 42684
SAVINGS:
5%
SAVINGS:
5%
Electricity
& GAS
N.B. The savings in electricity represent 0,24% of CERN’s Total Electricity consumption [990’895 MWh/year]
PLAN

## Slide 14
Summary
14
PLAN
ACHIEVEMENT
FUTURE PERSPECTIVES
Introduction
Conclusion
Solutions proposed in 2022: application in winter season 22-23
Led installation
Shutdown of public lights at nights
No electrical radiators
Optimization of the heating district
User awareness: good behaviour – HSE Campaign
Focus on electricity consumption
Focus on gas consumption
Sustainable heating plants
Cooling strategy

## Slide 15
Electricity
Starting date: 09/01/2023
LEDs INSTALLATION CAMPAIGN**
Manpower increased by 2 FTE in February 2022
**Please note that these data comes from a calculation, not from invoices
Chart: LEDs installation - Energy savings 2023
| 44935 | 45078
 | 0 | 254.94
TODAY:
Savings: 283 MWh
LED Installed: 10’260
EXPECTATIONS
DECEMBER 2023:
LED to be Installed: 28’000
Investment costs | [CHF] | 730’000
Objective of reduction | [MWh/year] | 1’992
Energy savings costs | [CHF/year] | 228’000
Scale of application | 23% of total LED number in Meyrin and Prevessin | 
Impact on Users | None | 
ACHIEVEMENTS
After one year from the installation
Notes: 4%

## Slide 16
PUBLIC LIGHTING SHUTDOWN**
ACHIEVEMENTS
Electricity
Starting date: 11/10/2022
The public light has been shutdown every night from 11 p.m. to 5 a.m.
TODAY
IMPACT ON CERN’S ELECTRICITY CONSUMPTION:
Year 2022 (Oct.22 to Dec22): 36,7 MWh  0,07 % Annual reduction
Year 2023 (Until Today) 106.56 MWh  0,22 % Current Reduction
(Jan23 to Dec23) 262.8 MWh  0,54 % Annual reduction
**Please note that these data comes from a calculation, not from invoices
2022
2023
16
Notes: Waiting for more data - Nicolas Bellegarde

## Slide 17
Summary
17
PLAN
ACHIEVEMENT
FUTURE PERSPECTIVES
Introduction
Conclusion
Solutions proposed in 2022: application in winter season 22-23
Led installation
Shutdown of public lights at nights
No electrical radiators
Optimization of the heating district
User awareness: good behaviour – HSE Campaign
Focus on electricity consumption
Focus on gas consumption
Sustainable heating plants
Cooling strategy

## Slide 18
CERN Site Comparison in gas consumption: 2021 vs. 2022
ENERGY SAVING POLICY 2022
YEAR 2021 [MWh] | 68,971.73
YEAR 2022 [MWh] | 50,048.92
Savings [MWh] | 18,922.81
% Reduction | 27%
Chart: Gas consumption 2021 [68,971.73 MWh/year]
| Meyrin | Prevessin
Gas consumprtion | 55814.8641 | 13156.864
Chart: Gas consumption 2022 [50,048.92MWh/year]
| Meyrin | Prevessin
Gas consumprtion | 5341.9001 | 1447.618
BILL 2021 [CHF/year] | 2,73 Millions
BILL 2022 [CHF/year] | 2,65 Millions
Savings [CHF/year] | 0,08 Millions
Source: SCE-SAM Gas Invoices
ACHIEVEMENTS

## Slide 19
CERN Site Corrected comparison in gas consumption: 2021 vs. 2022
ENERGY SAVING POLICY 2022
YEAR 2021 [MWh] | 64,484.4
YEAR 2022 [MWh] | 51,917.7
Savings [MWh] | 12,550.8
% Reduction | 19%
DJ [DEGRÉ JOUR] = DJ make it possible to weight the energy consumption according to the climate. The climate correction consists of weighting the heating consumption on the annual climate data of the weather station. The goal is to make the years comparable with each other, regardless of the harshness of winter.
YEAR 2021 [MWh] | 68,971.7
YEAR 2022 [MWh] | 50,048.9
Savings [MWh] | 18,922.8
% Reduction | 27%
Real consumption vs. Corrected consumption
Looking at the Corrected consumption, we can see that, erasing the climatic variable, CERN gas consumption in 2022 decreased.
The Reference DJ for the calculation comes from an average of 20 years of data (2000-2022), for a range of 12/18°C
Source: Office cantonal de l'énergie - OCEN
SCE-SAM Gas invoices
Without the influence of the climate
Without the influence of climate
ACHIEVEMENTS
Notes: Hot wave in may
External temperature is less than 12°C
It is a difference between the external temp and a reference temp that allows the estimation of the energy consumption in the buildings.
So
Le degré jour unifié (DJU) est la différence entre la température extérieure et une température de référence qui permet de réaliser des estimations de consommations d'énergie thermique pour maintenir un bâtiment confortable en proportion de la rigueur de l'hiver ou de la chaleur de l’été
mma estesa a tutti i giorni della differenza positiva di temperatura tra una fissata (18) e la temp media esterna giornaliera

## Slide 20
Meyrin Site Comparison in gas consumption: winter seasons 21-22 vs 22-23
Run of the Heating District:
Season 2021-22: October 2021 - May 2022
Season 2022-2023: November 2022 – April 2023
Reduction from winter 21-22 to winter 22-23: - 38%
Gas consumption [MWh] |  |  | Saving
Month | 2021-2022 | 2022-2023 | MWh
October | 5,278.0 | 149.5 | 5,128.51
November | 7,422.3 | 3,906.4 | 3,515.85
December | 9,670.6 | 5,341.9 | 4,328.75
January | 9,751.8 | 6,516.4 | 3,235.39
February | 7,653.7 | 6,499.6 | 1,154.13
March | 7,062.0 | 5,975.2 | 1,086.82
April | 5,187.4 | 4,313.6 | 873.81
May | 1,042.0 | 0.0 | 1,042.02
TOTAL | 53,067.9 | 32,702.6 | 20,365.26
From SCE-SAM Gas Invoices:
Without the influence of climate
Total corrected reduction from winter 21-22 to winter 22-23: -31%
ACHIEVEMENTS

## Slide 21
Meyrin Site
Consumption vs Expenses – winter seasons 21-22 vs 22-23
Despite the decrease in the consumption of GAS, the bills have significantly increased.
Run of the Heating District:
Season 2021-22: October 2021 - May 2022
Season 2022-2023: November 2022 – April 2023
From SCE-SAM Gas Invoices:
ACHIEVEMENTS
Notes: Comparison 2 years gas consump

## Slide 22
From SCE-SAM Gas Invoices:
Without the influence of climate
Prevessin Site
Comparison in gas consumption: winter seasons 21-22 vs 22-23
Gas consumption [MWh] |  |  | Saving [MWh]
Month | 2021-2022 | 2022-2023 | 
October | 1,127.0 | 36.5 | 1,090.5
November | 1,596.4 | 1,093.2 | 503.1
December | 2,242.9 | 1,447.6 | 795.3
January | 2,378.2 | 1,684.0 | 694.1
February | 1,697.1 | 1,542.1 | 155.0
March | 1,525.4 | 1,341.3 | 184.1
April | 1,403.1 | 980.3 | 422.8
May | 367.3 | 0.0 | 367.3
TOTAL | 12,337.4 | 8,125.1 | 4,212.3
Reduction from winter 21-22 to winter 22-23: - 34%
Run of the Heating District:
Season 2021-22: October 2021 - May 2022
Season 2022-2023: November 2022 – April 2023
Total corrected reduction from winter 21-22 to winter 22-23: -25%
ACHIEVEMENTS

## Slide 23
Prevessin Site Consumption vs Expenses – Winter seasons 21-22 vs 22-23
Despite the decrease in the consumption of GAS, the bills have significantly increased.
Fixed future GAS Prices (Contract SDV17):
2024: 69.33 €/MWh
2025: 60.81 €/MWh
Run of the Heating District:
Season 2021-22: October 2021 - May 2022
Season 2022-2023: November 2022 – April 2023
From SCE-SAM Gas Invoices:
ACHIEVEMENTS

## Slide 24
Expectations vs. Reality
Chart: Expectations [Calculation made in Sept 2022] GAS SAVINGS [MWh/year]
| Gas consumption in 2021 | Energy saved per year
 | 62137 | 3555
ACHIEVEMENTS
MEMO BY HSE
BILL 2021 [CHF/year] | 2,73 Millions
BILL 2022 [CHF/year] | 2,65 Millions
Savings [CHF/year] | 0,08 Millions

## Slide 25
Summary
25
PLAN
ACHIEVEMENT
FUTURE PERSPECTIVES
Introduction
Conclusion
Solutions proposed in 2022: application in winter season 22-23
Led installation
Shutdown of public lights at nights
No electrical radiators
Optimization of the heating district
User awareness: good behaviour – HSE Campaign
Focus on electricity consumption
Focus on gas consumption
Sustainable heating plants
Cooling strategy
Notes: Meyrin: G:\Departments\SMB\Groups\SE\HE\HE HVAC\Batiments\200\2022_heating_plant_upgrade\DCE\Steering_board
Prevessin: G:\Departments\SMB\Groups\SE\HE\HE HVAC\Batiments\776 - Nouvelle chaufferie\02_DCE\Steering_board

## Slide 26
SUSTAINABLE HEATING PLANT
Meyrin Heating Plant
FUTURE PERSPECTIVES
Objectives:
Renovation of the heating distribution components in B200 & 201.
Arrangement of technical room in B200 for housing the heating pump.
Installation and connection of the heating pump.
Pipes connection from HP to PA1.
Delivery expected for hot season 2026-27
SF1
COOLING TOWER
PA1 LHC
CURRENT CONFIGURATION (200 & 201)
3 boilers supplying the heating district in Meyrin Site
PROJECT:
HEAT PUMP INSTALLATION
To recover energy from the cooling tower SF1, covering the main heating needs on the Meyrin site.
HEAT PUMP
Notes: To achieve the goal of carbon neutrality in 2050, any upgrade or change of the heating plant has to consider both the cost and level of CO2 emissions of the future energy, its transport and infrastructure. Ideally, any heating network should be based on diverse energy sources, e.g. recovering heat produced on site and integrating renewable energy sources such as solar energy, geothermal, biomass, biodegradable waste, biogas, bio-oil, heat pumps, and electricity produced from renewable energy sources
Heat pump to be conn to accelerator cooling system to recover energy
PA1 Atlas
The proposed project will reuse the fatal energy from SF1 with heat pumps powered by electricity, resulting in a much-reduced carbon emission and a raise of the renewable energy rate, following the European and French directives about energy efficiency.
The new heating plant proposal ensures the main power via heat pumps, to cover the major part of the current heating needs on the Meyrin site, backed up by gas boilers which will also cover the power peaks in the coldest days. The energy source for the heat pumps is SF1
t P1

## Slide 27
SUSTAINABLE HEATING PLANT
Meyrin Heating Plant– Design overview
FUTURE PERSPECTIVES
Meyrin Site
201
200
SF1
PROJECT: HEAT PUMP INSTALLATION
To recover energy from the cooling tower SF1, covering the main heating needs on the Meyrin site.
SF1
Heating Plant
3 boilers, 15 MW each (existing).
1 heat pump 8 MW
Available place for additional heat pump, if needed
New Heat Pump
Notes: How much in terms of savings (gas and CO2) now vs future

## Slide 28
  Flexibility with gas boilers
SUSTAINABLE HEATING PLANT
Meyrin Heating Plant - Advantages
FUTURE PERSPECTIVES
The boilers will represent a backup for the HP, for the power peaks in the coldest days
  Compliance with European directives regarding the Carbon Neutrality goal by 2050: increase in renewable energy rate and reduction in CO2 emissions.
  N.B. The goal is to work on the decrease of the peaks of installing a bigger Heat Pump.
Chart: CO2 emissions: evolution by 2050
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Cumulative CO2 HP+Gas [tCO2] SC1 | 10766.0947 | 21532.1894 | 32298.2841 | 43455.2774 | 54612.2708 | 65769.2641 | 70550.5174 | 75331.7706 | 80113.0238 | 84894.2771 | 89675.5303 | 94456.7835 | 99238.0368 | 104019.29 | 108800.5432 | 113581.7964 | 118363.0497 | 123144.3029 | 127925.5561 | 132706.8094 | 137488.0626 | 142269.3158 | 147050.5691 | 151831.8223 | 156613.0755 | 161394.3287 | 166175.582 | 170956.8352 | 175738.0884 | 180519.3417
Cumulative CO2 Gas 100% [tCO2] | 10766.0947 | 21532.1894 | 32298.2841 | 43455.2774 | 54612.2708 | 65769.2641 | 76926.2575 | 88083.2509 | 99240.2442 | 110397.2376 | 121554.231 | 132711.2243 | 143868.2177 | 155025.2111 | 166182.2044 | 177339.1978 | 188496.1911 | 199653.1845 | 210810.1779 | 221967.1712 | 233124.1646 | 244281.158 | 255438.1513 | 266595.1447 | 277752.1381 | 288909.1314 | 300066.1248 | 311223.1182 | 322380.1115 | 333537.1049
Notes: How much in terms of savings (gas and CO2) now vs future
Goal: to decrease the peaks (energy needs) instead of installing a bigger HP to cover the whole need
Optimization heating district to minimize the peaks and to cover max power with heat pump

## Slide 29
SUSTAINABLE HEATING PLANT
Prevessin Heating Plant
FUTURE PERSPECTIVES
Objectives:
New Building 776 for housing the heating plant;
Installation new heating plant with gas boilers and heat pump;
Dismantle the current heating installation in Building 860.
Delivery expected for hot season 2026-27
B.860
PCC, B.775
Building 776
New building, hosting the heating plant
Notes: Meyrin: G:\Departments\SMB\Groups\SE\HE\HE HVAC\Batiments\200\2022_heating_plant_upgrade\DCE\Steering_board
Prevessin: G:\Departments\SMB\Groups\SE\HE\HE HVAC\Batiments\776 - Nouvelle chaufferie\02_DCE\Steering_board

## Slide 30
SUSTAINABLE HEATING PLANT
Prevessin Heating Plant – Design overwiew
FUTURE PERSPECTIVES
Heating plant configuration:
  2 boilers, 1-2MW & 1-4 MW
  1 heat pump 2.5 MW
  Available place for additional boiler & heat pump, if needed
Building 776
New building, hosting the heating plant
Building 775
Hosting PCC, to be connected for the heat recovery
Building 860
Hosting old heating plant, to be dismantled
Gallery 818
Networks to be connected
776
775
New Heat Pump
PCC Heat exchangers
Notes: (1 of the boilers 4MW equipped for injector for Gas&Fuel, not only gas, in case of gas crisis

## Slide 31
Heat pump = 80%
  Flexibility with gas boilers
SUSTAINABLE HEATING PLANT
Prevessin Heating Plant - Advantages
FUTURE PERSPECTIVES
The boilers will represent a backup for the HP, for the power peaks in the coldest days
  Compliance with European directives regarding the Carbon Neutrality goal by 2050: increase in renewable energy rate and reduction in CO2 emissions.
  N.B. The goal is to work on the decrease of the peaks of installing a bigger Heat Pump.
80% Heat pump
Heating power profile along a typical year
Notes: Gas price in 2021 with increase rate 2.5 % every year
Meyrin old value before update heating
Goal: to decrease the peaks (energy needs) instead of installing a bigger HP to cover the whole need
Optimization heating district to minimize the peaks and to cover max power with heat pump

## Slide 32
Summary
32
PLAN
ACHIEVEMENT
FUTURE PERSPECTIVES
Introduction
Conclusion
Solutions proposed in 2022: application in winter season 22-23
Led installation
Shutdown of public lights at nights
No electrical radiators
Optimization of the heating district
User awareness: good behaviour – HSE Campaign
Focus on electricity consumption
Focus on gas consumption
Sustainable heating plants
Cooling strategy

## Slide 33
COOLING – SCE Consolidation strategy
FUTURE PERSPECTIVES
The goal is to replace obsolete chillers by new ones with low greenhouse effect gas, to increase efficiency and energy recovery potential.
Building 40 – In progress
Refurbishment of the chilled water production
153 Cluster – In progress
New CW production and distribution network
Building 501 – Completed
Refurbishment of chilled water production
  SCE Memorandum – EDMS: 2084349 v.2.4
Notes: 2084349 v.2.4

## Slide 34
Conclusion
34
Significant reductions since September 2022: Introduction of Energy Saving Policy
Strong influence of the climate in the reduction of the gas consumption
Climate change: a sensitive topic worldwide
Challenge: to maintain the trend in the following years
ANY QUESTIONS?
Notes: The reduction in the GAS consumption at CERN has been significant since the introduction of the Energy Saving Policy in September 2022. The optimization of the Heating District led to a big reduction in consumption, but it is important to consider that its functioning is strictly related to the temperature pattern, which could vary in the following years.
The benefits also come from a stronger awareness of the importance of energy savings. The topic has now become sensitive worldwide, but it was previously not valued enough.
Therefore, if this first attempts to decrease the consumption at CERN have been “easier” to accomplish, in the following years the challenge will be to search for new solutions to maintain the trend.