## Slide 1: CERN future projects, Cryogenics for superconductivity
Serge CLAUDET, as deputy Cryogenic group leader & HiLumi Cryo WP leader
CERN, 29th Jan’20

## Slide 2
CERN present infrastructure and future projects
From LHC to HiLuminosity LHC
and behond …
LHC ring:
27 km circumference
Notes: 2

## Slide 3
Nominal luminosity
Peak Luminosity
“ The potential of the facility”
Performance
Integrated Luminosity
“What allows science” (statistics)
Qualification – Global availability - Time
today
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 4: Towards higher collision rates
Luminosity = f * N2 / 4p s2
stronger focusing
LIU
More intensity
New discoveries or precision measurements need integrated luminosity !!!

## Slide 5: The most straight forward action: reducing beam size with a «local» action
Quadrupole triplet and D1
Smaller   larger IT aperture
With stronger gradients
LHC has better aperture than anticipated: now all margin can be used; however is not possible to have  < 40 cm
To increase Luminosity
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 6: HL-LHC configuration
HL-LHC
Existing LHC
NC D1
SC D1
Corrector
Package
Q1
Q2a
Q2b
Q3
D2
Q4
CC
HL-LHC relies on more powerful final focussing quadrupoles, associated recombination dipoles and crab cavities,
Local heat loads expected x5 w.r.t LHC
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 7: HL-LHC cryogenic upgrade
+
P1-P5: 2 new cryoplants (~15 kW @ 4.5 K incl. ~3 kW @ 1.8 K ) and 2 x 750m cryo-distribution for high-luminosity insertions
P4: upgrade (+2 kW @ 4.5 K) of an existing LHC 18 kW @ 4.5K cryoplant
SPS-BA6: SRF test facility with beam primarily for Crab-Cavities
SPS-BA6
Other test facilities related activities not reported here
P1/P5: Provide adequate cooling for this
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 8: P1/P5 Cryogenic architecture
QSCG
QSVB
QSDQ
QSRG
QSDN
QSAG
QURCG
QPLG
QXL
DFHM
DFHX
QSP
GHe storage tanks
Dryer
Liquid Nitrogen tank(s)
Surface cold box
Vertical transfer line
Quench tank
Surface piping
Warm compressor station
DSHX
DSHM
DSL
Q1
Q2b
Q3
CP
D1
D2
CC
CC
Q4
Q5
Q6
HRL
QRP
QPP
SHE
SHM
SD
US
SLN
SLN
Q2a
Surface
Shaft
Underground
15 kW equivalent at 4.5 K, including 3 kW at 1.8 K
Cold compressors box
QUIG
Interconnection box
UR
UL
DFBL
(existing)
CC
CC
LHC tunnel
DFX
DFM
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 9: Cryo-distribution reference
IT-D1
D2
CC
QRL-QXL
Reference established, optimised considering project requirements and CRG expertise
Identification of needs,
Proposal of a possible architecture
Proposal of a reference configuration with size
3D models
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 10: QXL cryoline, 3D models and integration
1’500m, 5 tubes in a shell diam 650-800mm, similar to existing LHC QRL cryoline
Tender 2021,
Following 60m demonstrator mid 2020
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 11: From cooling requirements to Refrigeration capacity and process
Load @
4.5-20K
Load @
40-60K
Load @
4.5-300K
Load @
1.9-2K
LC
HX
40 K
60 K
4,5 K
20 K
300 K
4 K
D
C
E
B
F
QSRG
QURCG
QSCG
QPLG
Obvious need for 15mbar header (1.8K cold source), no special need for 4.5K loads
Process options now under study
Pulsed loads @ 1.9K !!!
(4 CC’s)
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 12: 2 x 15 kW eq. @ 4.5K He Refrigerators, incl 3kW @ 1.8K
Tender Q1 2021
S. Claudet - Jan'20
CERN future projects, Cryogenics
Best Capex + Opex offer matching specified requirements
Compressors, dryers, cold box(es), vertical cryoline, cold compressors

## Slide 13: Complementary infrastructure
Valve boxes (2): 25 valves in a 2m Diam & 8-10m long box
GHe storage tanks (4): 250 Nm3 – PN25
LN2 storage tanks (2): 50’000 l + vaporiser
Interconnecting piping: 2’000m Diam 250 eq. stainless steel
Instrumentation for tunnel equipment (accuracy, radiation)
Controls (integration with existing LHC infrastructure)
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 14: Major civil engineering required at P1-P5
POINT 1
POINT 5
S. Claudet - Jan'20
CERN future projects, Cryogenics
All underground infrastructure being prepared during LS2

## Slide 15
Inventory of the surface works (P1, ATLAS)
All surface buildings during Run3
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 16
PHASE 1
Run 2
Run 3
LS 2
LS 4
LS 5
LS 4
LS 5
Run 5
LS2 starting in 2019 => 24 months + 3 months BC
LS3 LHC: starting in 2024 => 30 months + 3 months BC
Injectors: in 2025 => 13 months + 3 months BC
Beam commissioning
Technical stop
Shutdown
Physics
LHC roadmap
Run 3
LIU installation
LS 3
PHASE 2
Run 4
HL-LHC installation
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 17: Neutrino Platform (new extension of North Area)
LBNF/DUNE project in USA:
single-phase
proto-DUNE
dual-phase
proto-DUNE
Neutrino platform as a test area with charged beams for neutrino detectors (e.g. R&D for large liquid argon detectors).
Recently done at CERN
Larg.,
USA
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 18
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 19
CLIC: multi-TeV e+e- linear collider
100 MV/m accelerating gradient needed
for compact (~50 km) machine at 3 TeV
based on normal-conducting
accelerating structures and a two-beam
acceleration scheme
1 ab-1
2.5 ab-1
5 ab-1
Technically, construction could start in ~2026 (TDR in 2025)  first collisions at √s=380 GeV
in ~2035  25-30 years of physics exploitation
Cu !

## Slide 20: Cryogenics for ILC; TDR Design
Damping Rings
Polarised electron source
E+ source
Ring to Main Linac (RTML)
(including
bunch compressors)
e- Main Linac
e+ Main Linac
Parameters | Value
C.M. Energy | 500 GeV
Peak luminosity | 1.8 x1034 cm-2s-1
Beam Rep. rate | 5 Hz
Pulse duration | 0.73 ms
Average current | 5.8 mA (in pulse)
E gradient in SCRF acc. cavity | 31.5 MV/m +/-20% Q0 = 1E10
10 cryogenic plants
19 kW @ 4.5 K
including 2.4 kW @ 2 K;
10 technical sites;
84 t of helium inventory;
cryogenic distribution line
Updated proposal: 50% of nominal energy;
6 cryogenic plants in 1st phase
HeII,
JP
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 21
Future Circular Collider Study
International FCC collaboration (CERN as host lab) to study:
~100 km tunnel infrastructure in Geneva area, linked to CERN
e+e- collider (FCC-ee), as potential first step
pp-collider (FCC-hh)  long-term goal, defining infrastructure requirements
HE-LHC with FCC-hh technology
~16 T  100 TeV pp in 100 km
Up to 1’000 kW eq. @ 4.5K
800 t He
2018 CDR (studies involving industry)
2020 European Strategy (discussion)
S. Claudet - Jan'20
CERN future projects, Cryogenics

## Slide 22
Les accélérateurs sont notre coeur de métier
L’électricité est notre énergie,
L’Hélium est notre sang !
Merci pour votre attention!
S. Claudet - Jan'20
CERN future projects, Cryogenics