## Slide 1: EN/CV – Cooling and Ventilation of Large-scale Projects & Sustainability
Francesco Dragoni, Ingo Ruehl
Einstein Telescope Meeting - 18.10.2023

## Slide 2: Cooling & Ventilation (CV) Installations

## Slide 3: CV Systems Overview
    Power and control cubicles for CV Systems
    Water cooling systems sump pumps and firefighting network for technical buildings and underground areas
    Compressed air production and distribution
    Ventilation and air conditioning for technical buildings and underground areas
    Detector cooling

## Slide 4: CV Systems – Cooling Plants
30 Cooling towers (Total: 470 MW)
40+ Chilled Water Stations 6-12 °C
160+ Cooling Stations: raw & demi water, C3F8, C6F14, CO2, N2
800+ km pipework
Raw water distribution network: 3 station @ 5,400 m3/h
1,260 m3/h peak water consumption

## Slide 5: CV Systems – Ventilation and networks
1,500 + Air Handling Units
2,000 to 120,000 m3/h
800+ firefighting hydrants/valves
14 compressed air stations 200+ km distribution network
Demineralised water production: 20 m3/h at 0.1 uS/cm

## Slide 6: Computational Fluid Dynamics (CFD) Team

## Slide 7: I. Underground Ventilation - Sizing
Operational modes
Heat loads/humidity control
Minimum flow
Air speed
Dimensioning Criteria
LHC ventilation scheme
Operating mode | Design flow rate [m3/h] | Current supply flow rate [m3/h] | Current return flow rate [m3/h]
Tunnel Accessible | 18,000 | 18,000 | 23,000
Tunnel not accessible | 36,000 | 18,000 | 23,000
Emergency mode | 64,000 | 36,000 | 64,000
Reduced consumption | 9,000 | 9,000 | 10,000

## Slide 8
2 Possible Solutions
Cold beams
1 - Natural convective cooling
17
21
25
29
33
Muon chambers target temperature range: 18-25 °C
ATLAS UX15 Cavern
Air Temperature [°C]
II. ATLAS UX15 Cavern - Destratification
2 - Active
mechanical cooling
8 Air Handlers

## Slide 9
II. ATLAS UX15 Cavern - Destratification
UX15 Air Temperature
with Air Handlers [°C]
Muon chambers target temperature range: 18-25 °C
ATLAS UX15 Cavern
Air Temperature [°C]
17
21
25
29
33
2 - Active
mechanical cooling
8 Air Handlers

## Slide 10
II. ATLAS UX15 Cavern - Destratification
Muon Chambers Temperature Measurements
Destratification OFF
Destratification ON

## Slide 11: III. CEDAR Detector – Temperature stability
TIN = 23.0 °C ± 0.1 K
Standard system: ± 1 K
Requirement
CEDAR Detector

## Slide 12: III. CEDAR Detector - Ventilation System
Run 2015
Run 2018
Temperature Stability
± 0.1 K
Required
vs
± 1.0 K
Standard solution
± 0.08 K
Achieved

## Slide 13: IV. Gas management in underground
Ventilation systems
CFD Analysis

## Slide 14: IV. Gas management in underground
Ventilation systems
CFD Analysis
IDTL
TWA
STEL INRS
STEL Suva
10.000 m3/h
10.000 + 3.750 m3/h
10.000 + 7.500 m3/h
Y = 1 m from false floor

## Slide 15: V. Water rising systems
Cooling circuits drains
Underground drain water
Hydrocarbon presence
High pH
Water treatment
Potential issues
Requirements
Suspension particles
Contaminated water
Underground toilets
Main sump
3 pumps
Backup sump
2 pumps (1+1)
PM32 water rising system
Critical system
80 m3/h underground water infiltration

## Slide 16: Cooling and Refrigerant

## Slide 17: ATLAS/CMS - Si detector cooling chain
detector cooling plant
transfer lines
distribution
heat sink
primary chiller plant
cooling towers
EN-CV
EN-CV
(NTNU + EP-DT)
EP-DT
EXP-TC
(EP-DT)
Experiment
(EP-DT)
Experiment
Courtesy P. Hanf

## Slide 18: ATLAS/CMS - R744 Cooling Systems
ATLAS and CMS cooling: same concept, same hardware & different distribution
A Primary lubricated loop (purple lines)
A Secondary Oil free distribution loop (red lines)
Courtesy P. Hanf

## Slide 19: ATLAS/CMS – Detector cooling timeline
RUN 4
RUN 3
R744 (CO2)
Secondary circuit "coolant” technologies
Primary circuit “Refrigerant” technologies
Today
RUN 2
RUN 1
2008
2029
CO2 -2PACL technology 1kW @-30°C, 2Plants
*C3F8 62 kW@-25°C, 1 Plant
*C6F14 101 kW below -20°C, 5 Plants
CO2 -2PACL technology 17.5 kW below -25°C, 6Plants
*C3F8 62kW@-25°C, 1 Plant
*C6F14 91 kW below -20°C, 4 Plants
CO2 -2PACL technology 23.5 kW below -30°C, 6Plants
CO2 -2PACL technology 1 130 kW @ -53°C, 2Plants
*R404a/R507a & R448a
*R404a/R507a
*Chemical products damaging environment and contributing to the Global warming
June 2023 - Update the F-gas regulation (EU 517/2014) prohibiting or controlling the use of chemical refrigerant
Courtesy P. Hanf

## Slide 20: ATLAS/CMS - R744 Cooling Systems
R744 Cooling Slice
Production
module
Production
module
Common module
Common module
Control & Power supply
Control
&
Power supply
Aircoolers part
of the compressor slice
ATLAS SXSN1 Building – Final system with 7 slices

## Slide 21: Future Circular Collider (FCC)

## Slide 22: FCC layout
Courtesy A. Navascues Cornago
FCC-ee machine elements
AC terminals
Smoke/He extraction plenum
Fresh air passage
No return duct
Pipework
FCC-ee underground structure

## Slide 23: FCC Ventilation Principle
FCC sector ventilation
Thermal aspects in FCC sector
AC terminals
Smoke/He extraction plenum
Operation modes
Courtesy G. Peon

## Slide 24
Q&A?