## Slide 1
Tobias Stadlbauer
Special Magnets
MedAustron
30 March 2011
Special Magnets Controls
Status
Introduction
Details
Status
AOB
Components

## Slide 2
Content
Our components which need to be controlled
What has been done since last MACS Week
What items need to be done until completion
Interesting Details
AOB
Introduction
Details
Status
AOB
Components

## Slide 3
Controlled Components
Magnetic Septa and Chopper Dipole (10):
water flow,
water leakage,
coil temperature
Electrostatic Septa (2):
remote displacement system
Power supplies (9):
Set points,
trigger,
state control,
timing
CNAO model
Introduction
Details
Status
AOB
Components

## Slide 4
What has been done since last MACS Week
Common STATUS word between special magnet and normal power supplies and individual FAULT words
State diagram modified to incorporate new BIS interlock transition conditions
Decision for optical triggers to avoid EMI problems of electrical triggers
No PCO FED card tests from WP BTS:
use of direct trigger from MTS over optical fiber thus
no electrical PCO FED trigger used thus no reason for tests
BIS inputs and outputs for our systems are defined and fixed
Tune Kicker Controls defined
Updated Special Magnets Controls Compendium with latest information and comments
Introduction
Details
Status
AOB
Components

## Slide 5
What items need to be done until completion (rough)
MKC risk assessment – impact on controls interfaces
Displacement System for electrostatic Septa (PLC)
PLC-System for Water, Temperature Control/Interlock
Fast Deflector power supply controls
RS422 error detection implementation
Upcoming task during production like verification, validation, contract follow up
Introduction
Details
Status
AOB
Components

## Slide 6
What items need to be done until completion (detail)
Introduction
Details
Status
AOB
Components
Displacement System for electrostatic Septa (PLC) (0.5 FTE)
  Priority: intermediate
  Manpower: partly covered
PLC-System for Water, Temperature Control/Interlock (0.25 FTE)
  Manpower: partly covered
Fast Deflector Power Supply Controls (0.8 FTE)
  Priority: intermediate
  Manpower: arranged but not delivered yet
RS422 error detection implementation
  Requirements for manufacturer only
  Priority: high
  Manpower: covered
Upcoming task during production like verification, validation, contract follow up (0.2 FTE)
  Priority: currently low, situation will change in summer 2011
  Manpower: partly available
MKC Systems (> 0.5FTE):
  Definition if medical device
Priority: Very high
Manpower: not available
  risk assessment – impact on controls interfaces
Priority: Ultra high
Manpower: not assigned
  Definition of Safety level status
Priority: High
Manpower: only partly covered
  Definition of BDS and MACS interface
Priority: High
Manpower: partly covered

## Slide 7
What items need to be done until completion (detail)
Introduction
Details
Status
AOB
Components
Already the listed tasks are not covered by manpower. Any Additional task has to be postponed or postpones scheduled tasks until further resources are committed.
Committed Resources available for Controls Issues 2011:
Tony (CERN): 0.2 FTE (Consultancy, Planning, Management of CERN Resources)
Christoph (CERN): 0.2 FTE (Remote displacement systems only )
Tobias (MA): 0.7 FTE (Development, Planning )
Thomas (MA): overhead
Asked for (but not approved):
0.3 FTE Student
0.5 FTE MA Staff

## Slide 8
Universal State Machine for Power Supplies
New transition conditions for BIS inputs
Introduction
Details
Status
AOB
Components

## Slide 9
Tune Kicker Power Supply (PKT)
Start-Trigger
Stop-Trigger
MTR
PKT
RF
Pre-Trigger
MTV
MTH
Selection Horizontal, Vertical
FED
(PCO FED)
Time
Current
OFF | ? | ?
Control architecture for the Tune Kicker Power Supply (PKT)
Simplified pulse generator circuit
Current over Time for the Tune Kicker Magnet
Introduction
Details
Status
AOB
Components

## Slide 10
Start-Trigger
Stop-Trigger
MTR
PKT
RF
Pre-Trigger
MTV
MTH
Selection Horizontal, Vertical
FED
(PCO FED)
Time
Current
Command STANDBY
STBY | ? | ?
Introduction
Details
Status
AOB
Components
Tune Kicker Power Supply (PKT)

## Slide 11
Start-Trigger
Stop-Trigger
MTR
PKT
RF
Pre-Trigger
MTV
MTH
Selection Horizontal, Vertical
FED
(PCO FED)
Time
Current
Command STANDBY
Command Horizontal
STBY | H | ?
Tune Kicker Power Supply (PKT)
Introduction
Details
Status
AOB
Components

## Slide 12
Start-Trigger
Stop-Trigger
MTR
PKT
RF
Pre-Trigger
MTV
MTH
Selection Horizontal, Vertical
FED
(PCO FED)
Time
Current
Command STANDBY
Command Horizontal
Download Set point: Current
STBY | H | 2100A
Tune Kicker Power Supply (PKT)
Introduction
Details
Status
AOB
Components

## Slide 13
Start-Trigger
Stop-Trigger
MTR
PKT
RF
Pre-Trigger
MTV
MTH
Selection Horizontal, Vertical
FED
(PCO FED)
Time
Current
Command STANDBY
Command Horizontal
Download Set point: Current
Command ON
ON | H | 2100A
Tune Kicker Power Supply (PKT)
Introduction
Details
Status
AOB
Components

## Slide 14
Start-Trigger
Stop-Trigger
MTR
PKT
RF
Pre-Trigger
MTV
MTH
Selection Horizontal, Vertical
FED
(PCO FED)
Time
Current
Command STANDBY
Command Horizontal
Download Set point: Current
Command ON
Pre-Trigger
ON | H | 2100A
Tune Kicker Power Supply (PKT)
Introduction
Details
Status
AOB
Components

## Slide 15
Start-Trigger
Stop-Trigger
MTR
PKT
RF
Pre-Trigger
MTV
MTH
Selection Horizontal, Vertical
FED
(PCO FED)
Time
Current MTH
Command STANDBY
Command Horizontal
Download Set point: Current
Command ON
Pre-Trigger
Start-Trigger
ON | H | 2100A
Tune Kicker Power Supply (PKT)
Introduction
Details
Status
AOB
Components

## Slide 16
Start-Trigger
Stop-Trigger
MTR
PKT
RF
Pre-Trigger
MTV
MTH
Selection Horizontal, Vertical
FED
(PCO FED)
Time
Current MTH
Command STANDBY
Command Horizontal
Download Set point: Current
Command ON
Pre-Trigger
Start-Trigger
Stop-Trigger
ON | H | 2100A
Tune Kicker Power Supply (PKT)
Introduction
Details
Status
AOB
Components

## Slide 17
Tendering
Tendering documents for Magnets and Power supplies will be released end March 2011
MKC power supply thereby also the MKC controls are excluded from this tender
Tendering for electrostatic septa power supplies second half of 2011
Introduction
Details
Status
AOB
Components

## Slide 18
References
[1] J. Borburgh, M. Barnes, T. Fowler, M. Hourican, T. Kramer. T. Stadlbauer, Special Magnets - Final Design Report, CERN, 2010 (unpublished).
[2] J. Gutleber, R. Moser, MedAustron Control System Architecture and Design Document, MedAustron, ES-1000406-a-JGU.
[3] J. Gutleber, R. Moser, Main Timing System and Signal Distribution Services, MedAustron, unpublished.
[4] J. Borburgh, et al., “MedAustron Special Magnets - WP description”, CERN, Geneva, 2009
[5] M. Marchhart, T.Glatzl “Magnet Slow Control - Requirements”,
MedAustron
[6] T. Fowler, T.Stadlbauer “Special Magnets Controls Compendium”,
ES-110114-a-TST-V0.91
Introduction
Details
Status
AOB
Components