## Slide 1: Overview of the CO2 cooling DEMO obtained results and a prediction of future system behaviour
Viren Bhanot, Loic Davoine, Yann Herpin, Cedric Landraud, Jerome Noel, Youri Penders, Kzrysztof Sliwa, Dani Texeira, Bart Verlaat, Michal Zimny
29/05/2024

## Slide 2: Challenges & Goals

## Slide 3: Challenges for Phase 2
Operation temperatures down to -45°C
  -45°C close to CO2 triple point
  Increased gradients at lower temperatures
  Stable primary cooling is required in limited range temperature zones
High cooling capacities required
  300 kW for ATLAS  7 plants, 6 accumulators
  550 kW for CMS  9 plants, 8 accumulators
  Redundancy important for continuous operation
Need for surface facilities
  Smaller accumulators in cavern, therefore surface storage of CO2
  Primary cooling system on surface, therefore large transferlines to service cavern
Energy efficiency considerations
  Improvement of energy efficiency with scaled up systems

## Slide 4: The cold challenge
Condenser
Pump
Flow control by-pass
1
2
3
4
9
11
Accumulator
Evaporators
Transferline (~100m)
5
6
7
8
10
2PACL plant
A cold and very stable primary cooling is needed
T variation
Minimum liquid temperature
Sub cool margin
Detector outlet
Detector inlet
Plant
PP2 Manifold
From -30°C to -40 °C the gradients double!

## Slide 5: The surface challenge
2PACL cooling plants located in USA-15 / USC-55 underground
Detector evaporator loops are connected via manifolds and concentric transfer lines to the 2PACL plants
The 2PACL plants are cooled by the primary R744, which is located on the surface
The primary R744 plants are cooled by water from the towers and air cooling
Surface storage of CO2 to control the charges of the underground 2PACL plants
Water cooling tower
Trans critical CO2-primary
Service cavern
Experimental cavern
Multiple 2PACLs with reduced accumulator
Refrigerated low pressure surface storage of CO2
80m
Manifolds
and distribution
Air cooled & low power back-up chiller
to keep surface storage pressure low
+15/-20°C
-53°C
Down to -20°C
+15 to -45°C
27°C
Up to 100°C
+15 to -40°C
+ Dry-air and vacuum systems
ATLAS
CMS
Uninsulated transfer lines
  Requires warm liquid supply and warm return gas to cavern to avoid condensation
Reduced accumulator sizes
  Good interaction required between cavern plants and surface storage

## Slide 6: Scaled-up DEMO system
DEMO
Full scale system containing all system elements
Real size plant and accumulator
Short low-capacity transferline
100 kW dummy load to simulate detector heat
Able to circulate 1.58 kg/s of CO2
Includes one-head back-up plant for redundancy swap
Surface Storage Simulator unit
R744 primary
Accumulator
3H-Plant
Back-up Plant
Transfer line
Control cabinets
Surface storage simulator
Safety exhaust
Dummy load

## Slide 7: Challenges for Phase 2
High cooling capacities required
  300 kW for ATLAS  7 plants, 6 accumulators
  550 kW for CMS  9 plants, 8 accumulators
  Redundancy important for continuous operation
Need for surface facilities
  Smaller accumulators in cavern, therefore surface storage of CO2
  Primary cooling system on surface, therefore large transferlines to service cavern
Energy efficiency considerations
  Improvement of energy efficiency with scaled up systems
Operation temperatures down to -45°C
  -45°C close to CO2 triple point
  Increased gradients at lower temperatures
  Stable primary cooling is required in limited range temperature zones
  Demonstrate operation with 100 kW cooling power at -45°C at the plant
  Demonstrate automatic procedures
  Demonstrate the new method of accumulator flow-through (2PACL-FT)
  Demonstrate specific design updates
    Surface storage interaction
    A reliable accumulator level control
  Demonstrate the warm return of the R744 gas (R744 transfer is without insulation)
  Demonstrate stable operation in all conditions, especially at cold temperatures

## Slide 8: Operation and Performance

## Slide 9: Flow-through vs. non-flow-through
Pump
Traditional 2PACL
2-Phase
Subcooled liquid
Subcooled liquid
2-Phase
Super heated gas
Cooling = pressure decrease
No cooling = pressure increase
Only cooling is pressure controlled
CO2 sub cooler
R744 Evaporator
Pump
2-Phase
Subcooled liquid
2-Phase
Super heated gas
Cooling = pressure decrease
Heating = pressure increase
Heating and cooling is pressure controlled
CO2 Condenser / sub cooler
R744 Evaporator
Saturated liquid
Heater is only needed in special occasions
R744 cooling
R744 cooling
2PACL-FT
(Flow through Accumulator)
Subcooled liquid
Electrical heater
Diffuser
A good phase separation is needed not to cool the vapor with incoming cold liquid
Schematic by Bart Verlaat

## Slide 10: Typical system behavior in 2PACL-FT mode
Dummy load
Chiller
Subcooled liquid
Accu Tsat
Plant return
Chiller deviation due to high load
Accu deviation due to accu HX limitation
(More severe at low SP)
Perfect control of sub cooled liquid
Accu control and SC liquid following
2PACL-FT mode shows a very stable and easy to control system
It has a very good liquid temperature controllability so that at high temperature set-points there is no risk of cold drift anymore
  Very good experience with a liquid dT of only 5°C
No need to condense pump flow to -50°C, as a few degrees subcooling is sufficient
5°C liquid dT

## Slide 11: Accumulator Redesign
Plunger tube
Addition of a plunger tube to keep heat exchanger flooded
Installation of a Q-pipe in heat exchanger to improve flow distribution in the heat exchanger
Q-pipe
Flow distribution much better with Q-pipe
No Q-pipe shows liquid flowing through the back
Too little convective flow without a plunger tube
Plunger and Q-pipe have increased cooling capacity from 15 kW at -35°C to 50 kW at -45°C
Schematics by Yann Herpin

## Slide 12: Accumulator Redesign
Plunger tube
Addition of a plunger tube to keep heat exchanger flooded
Schematics by Yann Herpin
Installation of a Q-pipe in heat exchanger to improve flow distribution in the heat exchanger
Q-pipe
Aluminium Cast Heater Block
Control valve
Cast heater block temperature is kept constant and flow is regulated with a control valve
This concept keeps the heater surface warm and hence reduces moisture problems

## Slide 13: Heat Exchanger Configuration
Cold in
Warm out
Evaporator
Superheater
to Accu
from Detector
Warm return gas
Warm liquid from primary
Double HEX Configuration
Old HEX Orientation
Accu HEX Orientation
Plant HEX Orientation
Dew Point
Laminar-Turbulent transition

## Slide 14: Our performance goal: 100kW @ -45°C
DEMO chiller is not powerful enough to remain at -53°C above 60kW, slowly drift up
As a result of chiller drift, accumulator saturation also starts drifting at 70kW
Accu = -45°C
Accu = -40°C
The DEMO R744 chiller is not powerful enough to maintain -53°C above 60kW, a drift to -45 °C is observed at 100kW, and is therefore not able to cool down the accumulator sufficiently
Superheating
Superheating
Superheating collapse shows

## Slide 15: Our performance goal: 100kW @ -45°C
We have two heat exchangers operated in parallel on the accumulator
-45°C was kept at 50kW on a single heat exchanger!
With two heat exchangers, our goal of 100 kW at -45°C would be reached!
ATLAS maximum systems power: 60 kW; CMS maximum systems power: 90 kW
Injection valve has proper size
Accumulator heat exchanger reaches 50 kW at -45°C
Accu = -45°C

## Slide 16: Heat Exchanger Configuration
Cold in
Warm out
Evaporator
Superheater
to Pump
from Detector
Warm return gas
Warm liquid from primary
Double HEX Configuration
Old HEX Orientation
Accu HEX Orientation
Plant HEX Orientation
Dew Point

## Slide 17: Operation of the Condenser/Subcooler
Step of 30 kW induced
Valve opens quickly due to a ‘boost mode’
Valve opening is limited to ensure warm return gas
Subcooling is ensured and does not drop too low
  Recently implemented new control strategy ensures sufficient pump subcooling at -45°C at high and low load cases
    Dynamic dT setpoint only requests no more than what the chiller can provide in cooling
    Output high limiter on the valve to keep return gas warm
    ‘Boost mode’ implemented to speed up valve action at low subcooling
DTC setpoint
DTC setpoint decreases with available temperature differential
Accu setpoint change
Control strategy in action at 30 kW load step at -45°C in T2PACL
Plant HEX Orientation

## Slide 18: Operation of the Condenser/Subcooler
Step of 30 kW induced
Valve opens quickly due to a ‘boost mode’
Valve opening is limited to ensure warm return gas
Subcooling is ensured and does not drop too low
  Recently implemented new control strategy ensures sufficient pump subcooling at -45°C at high and low load cases
    Dynamic dT setpoint only requests no more than what the chiller can provide in cooling
    Output high limiter on the valve to keep return gas warm
    ‘Boost mode’ implemented to speed up valve action at low subcooling
Dew Point
Subcooling ensured in all detector cases !!
Plant HEX Orientation
Control strategy in action at 30 kW load step at -45°C in T2PACL
HEX slice target

## Slide 19: Surface Storage

## Slide 20: Surface Storage Concept
Accumulator
Condenser
Pump
Transfer line
Start-up by-pass
PV2a22
Flow control by-pass
CV1a16
3-Way selection
CV8078
Accu cooling
1
2
3
14
16
17
18
19
20
22
Surface Storage (SS)
23
24
15
21
Accu heating
SS cooling
SS heating
25
Surface Storage System
On surface
Accumulator Unit
Plant Unit
4
Evaporators
5
6
7
8
The surface storage is in fact 1 large common accumulator for all systems
The pressure is controlled by heating and cooling
  Electrical heating
  R744 branch cooling connection
  Small back-up chiller for maximum pressure safety

## Slide 21: Surface Storage Concept
Accumulator
Condenser
Pump
Transfer line
Start-up by-pass
PV2a22
Flow control by-pass
CV1a16
3-Way selection
CV8078
Accu cooling
1
2
3
14
16
17
18
19
20
22
Surface Storage (SS)
23
24
15
21
Accu heating
SS cooling
SS heating
25
Surface Storage System
On surface
In cavern
Accumulator Unit
Plant Unit
4
Evaporators
5
6
7
8
Thermosiphon loop
SS start up heater
SS pre cooling
The surface storage is in fact 1 large common accumulator for all systems
The pressure is controlled by heating and cooling
  Electrical heating
  R744 branch cooling connection
  Small back-up chiller for maximum pressure safety
The liquid must be brought underground, which goes by a natural convection thermosiphon
Several degrees sub cooling is needed before sending down the flow
A heater is present underground in return line to help start-up the convective flow

## Slide 22: Surface Storage Concept
Accumulator
Condenser
Pump
Transfer line
Start-up by-pass
PV2a22
Flow control by-pass
CV1a16
3-Way selection
CV8078
Accu cooling
1
2
3
14
16
17
18
19
20
22
Surface Storage (SS)
23
24
15
21
Accu heating
SS cooling
SS heating
25
Surface Storage System
On surface
In cavern
Accumulator Unit
Plant Unit
4
Evaporators
5
6
7
8
Thermosiphon loop
SS start up heater
SS pre cooling
SS supply
CV9s82
SS return
CV1s14
By-pass
PV9s82
to plants
The surface storage is in fact 1 large common accumulator for all systems
The pressure is controlled by heating and cooling
  Electrical heating
  R744 branch cooling connection
  Small back-up chiller for maximum pressure safety
The liquid must be brought underground, which goes by a natural convection thermosiphon
Several degrees sub cooling is needed before sending down the flow
A heater is present underground in return line to help start-up the convective flow
A supply valve is used to inject liquid at the condenser inlet, while a return valve is used to take liquid at the pump discharge

## Slide 23: Surface Storage Concept
Accumulator
Condenser
Pump
Transfer line
Start-up by-pass
PV2a22
Flow control by-pass
CV1a16
3-Way selection
CV8078
Accu cooling
1
2
3
14
16
17
18
19
20
22
Surface Storage (SS)
23
24
15
21
Accu heating
SS cooling
SS heating
25
Surface Storage System
On surface
In cavern
Accumulator Unit
Plant Unit
4
Evaporators
5
6
7
8
Thermosiphon loop
SS start up heater
SS pre cooling
The surface storage is in fact 1 large common accumulator for all systems
The pressure is controlled by heating and cooling
  Electrical heating
  R744 branch cooling connection
  Small back-up chiller for maximum pressure safety
The liquid must be brought underground, which goes by a natural convection thermosiphon
Several degrees sub cooling is needed before sending down the flow
A heater is present underground in return line to help start-up the convective flow
A supply valve is used to inject liquid at the condenser inlet, while a return valve is used to take liquid at the pump discharge
A discharge control valve keeps discharge pressure above surface storage pressure
A back-pressure regulation valve will allow detector pressure to be high, such that the accumulator can always be kept below surface storage pressure
SS supply
CV9s82
SS return
CV1s14
By-pass
PV9s82
Discharge control
CV1014
to plants
System BPR
CV8076

## Slide 24: Surface Storage 2PACL Operation
The Surface storage pressure underground is foreseen to work between 20 bar and 56 bar (~14-51 bar in SS-tank)
Discharge valve will keep discharge pressure 5 bar above surface storage setpoint, such that emptying will always be possible
Back pressure regulator (BPR) will be able to keep detector pressure at higher setpoints than surface storage setpoint, allowing us to keep the accumulator below surface storage setpoint
  This will allow us to always be able to fill
Surface storage and accumulator setpoints will be aligned as much as possible, but with multiple plants, BPR will be required in some cases
SS pressure
Accu pressure
Detector pressure
dP by BPR
Simulation by Viren Bhanot
SS=45 bar
SP=-40’C
1
2
24
SP=15’C
16
15
24
1,2
SS=45 bar
Pump outlet pressure
Setpoint change

## Slide 25: Accumulator Level Control
Implementation of level control will of the accumulator will keep the liquid level of the accumulator always in a specified range
If level is low, surface storage valves will open to fill the plant until accumulator reaches the desired level
Vice versa, if the accumulator level is high, surface storage emptying valve will regulate until level setpoint is reached
Pump speed will be boosted during emptying to keep detector flow steady
Level plot at -40°C accumulator setpoint and 20 bar surface storage pressure
Accumulator Level
Mass Flow
Detector dP
Pump Speed

## Slide 26: Pre-vaporization
Accumulator level rises at heat load increase
Surface storage will pump off the liquid
Pre-vaporization helps contain level
With Pre-vaporization
Without Pre-vaporization

## Slide 27: Pre-vaporization
Pre-vaporization helps contain level
With Pre-vaporization
0
0.1
0.2
0.3
0.4
0.5
0.6
0.7
Start vapor quality (-)
0
200
400
600
800
1000
1200
Density change as a function of start VQ and Tsat
in transfer line at a VQ increase of 0.3
Tsat=-50°C
Tsat=-40°C
Tsat=-30°C
Tsat=-20°C
Tsat=-10°C
Tsat=0°C
Tsat=10°C
Tsat=20°C
Pre-vaporizing to 5% necessary in a manifold heater when using a 50% accumulator
½ the density to accumulate = half accumulator size needed
Pre-vaporizing of the transfer line helps a lot, 5% VQ reduces the vapor volume with 50%
Accumulator charge reduction after pre vaporization and detector powering
With pre vaporization a power cycle will require less accumulator volume

## Slide 28: Plant and Accumulator start-up
Traditional Start-up Procedure
Start-up Procedure with Surface Storage
Detector Liquification
Detector Circulation
Accumulator Control
Operation
Surface Storage Pressure Equalization
Pump Liquification
Plant Circulation
Accumulator Skid Circulation
Detector Liquification (by BPR)
Detector Circulation
Accumulator Control
Operation
Plant Start-up
Accumulator Start-up
Start-up with surface storage starts from plant vapour state

## Slide 29: Plant and Accumulator start-up
Filling Accu using “Surface Storage”
System starts from empty
Cooldown
Liquefying detector
Power on
Setpoint change

## Slide 30: Back-up Plant Functionality
  Back-up plant is circulating in standby instantly kicks in and starts sending liquid to detector in case of main plant failure
  A temporary high flow is given due to the discharging of the higher pressurized back-up plant
  Pressure differential is maintained, and flow has not dipped to interlock values. Therefore, detector continues running during a swap
  Once the main plant is restarted, a swap takeover is performed in return, and the back-up plant returns to standby
Back-up plant
(running in stand-by)
Plants
To detector
Primary R744 chiller
Surface storage
Plant fails  swap to back-up
Plant is back  gradual takeover
Detector pressure & Tsat remain stable

## Slide 31: Summary & Conclusions

## Slide 32: Summary & Conclusions
The DEMO has successfully been operated full time since October 2022
  Including some technical stops for upgrades
Many aspects of DEMO operation have been thoroughly tested
Design load of 100 kW at -45°C is attainable
  Both in flow-through and traditional mode
Stable performance at different heat loads at -45°C has been achieved
  Heat exchanger performance considerably improved
  Flow-through mode tested and applied successfully as baseline operation
  Good control strategies for stable detector cooling at ultimate conditions
  Also good temperature control when in liquid
Surface storage interaction
  Accurate accumulator level control has turned out to be possible
  New start-up procedures have been run through using surface storage interactions
Back-up plant functionality has successfully been tested at different temperature setpoints and configurations

## Slide 33: Predictions for the Final Systems
Stable operation at temperatures from +15°C to -40°C at the detectors is expected from DEMO operation, irrespective of the load
Performance of DEMO meets foreseen detector heat loads, and the system is expected to handle heat load deviations and other perturbations well
With thorough commissioning campaign, good performance is expected throughout the final system lifetime

## Slide 34
Thank you!!
On behalf of the EP-DT team!

## Slide 35: The basic concept: 2PACL
Two-Phase Accumulator Controlled Loop  2PACL
Low vapor quality cooling for best heat transfer in small tubes
Large temperature range
  +20°C / -45°C
  Independent to applied heat load
Liquid loop start-up
  No thermal shocks
Very stable evaporator temperature control at a distance
  Detector Pressure ≈ Accumulator Pressure
All active control in distant plant in an accessible area
Successful in first LHCb Velo detector and Velo upgrades, CMS Pixel detector and ATLAS IBL

## Slide 36: Detector Specifications