## Slide 1: Flow distribution capillary tube testing for the CMS silicon detector upgrades Forum on Tracking Detector Mechanics 2024 Purdue University, Indianapolis, Indiana U.S.
Derek Jan Langedijk CERN, CMS Cooling Integration May 29th, 2024

## Slide 2: Content
Introduction
  The 2PACL Principle
  Capillaries in CO2 Cooling – Why?
Theoretical Prediction
  Principle
  Example
  Effectiveness & Difficulties
  Conclusion
Capillary Open System
  Working Principle
  Mechanical Design
In practise
  Capillary manufacturing
  Testing
  Consistency
Conclusion

## Slide 3: The 2PACL Principle – Components and Layout
Surface and underground layout
Schematic overview of 2PACL system
Surface and Underground layout with schematic system overview

## Slide 4: The 2PACL Principle – Thermodynamic Cycle
Components visualized in PH-Diagram

## Slide 5: Capillaries in CO2 Cooling – Why?
10 bar
~8 bar
~2 bar
Trigger Boiling
Passive Flow Distribution
Detector Loop Failure

## Slide 6: Theoretical Prediction – Principle
Prediction based on the Darcy-Weisbach equations modelled in MatLab
using Darcy-Weisbach:
Differential Pressure (∆p) [Pa]
Length of Tube (L) [m]
Darcy friction factor (fD) [-]
Density of the Fluid (ρ) [kg/m3]
Fluid Velocity (Wv) [m/s]
Hydraulic Diameter of the Tube (Dh) [m]
Inner Surface Roughness (e) [mm]
Reynolds Number (Re) [-]
fD during turbulent flow:
Reynolds number:
fD during laminar flow:

## Slide 7: Theoretical Prediction – Example from Detector List
Prediction based on the Darcy-Weisbach equations modelled in MatLab
Detector System
Sub-System
Capillary Properties
Desired
∆p
Capillary
Quantity

## Slide 8: Theoretical Prediction – Example from Detector List
Result Theoretical Prediction:
Super easy! Right…?

## Slide 9: Theoretical Prediction – Why is it still so difficult?
Capillaries are not perfect…

## Slide 10
Same Manufacturer!
Theoretical Prediction – Why is it still so difficult?

## Slide 11: Theoretical Prediction – Why is it still so difficult?
CT Scan on capillaries… BIGGER Inner Diameters

## Slide 12: Theoretical Prediction – Why is it still so difficult?
Overview of Results – Tolerance between +0.01mm and +0.03 mm
0.5mm
0.9mm
0.8mm
0.7mm
0.6mm

## Slide 13: Theoretical Prediction – Why is it still difficult?
How strong is a 0.05mm ID tolerance influencing the pressure drop?
Strong… 

## Slide 14: Theoretical Prediction – Why is it still difficult?
How strong is a 0.05mm ID tolerance influencing the pressure drop?
Small inaccuracies, make a big difference for pressure drop
0.624mm Capillary
2 bar decrease

## Slide 15: Theoretical Prediction – Why is it still difficult?
Coiling increases pressure drop. Also, coiling is subjective… see below:
Research is ongoing to better understand the effects of coiling on pressure drop!

## Slide 16: Theoretical Prediction – Testing each capillary!
Conclusion: Testing is a necessity; theory does not give sufficient accuracy.
Capillaries are not consistent:
Uncertainties with roughness
Uncertainties with inner diameter
Uncertainties with coiling
Solution: Build a test factory that can test all capillaries!

## Slide 17: Capillary Open System – Principle
Capillaries
  ∆p sensor
  Shut-off valves
Flow measurement and regulation
Bottle supply
Exhaust system (Single phase, gas)
Safety Burst Discs
Supply Subcooling
  Heat exchangers
  Bypass Valve
Subcooling regulator
Warm Nose Heater (ATLAS Only)
“2 Identical Setups for ATLAS and CMS”

## Slide 18: Capillary Open System – Principle
P&ID COS – Joao Noite, ATLAS Collaboration

## Slide 19: Capillary Open System – Mechanical Design
Original Design Liam Cooper Science & Technology Facilities Council, United Kingdom
Final Design
Martin Machac & Derek Jan Langedijk CERN

## Slide 20: Capillary Open System – Mechanical Design
Capillaries
Bottle connection
Capillary shut off valves
Heat exchangers
Exhaust system (water tank)

## Slide 21: Capillary Open System – Constructed @ CERN
February 2023
Commissioning with ATLAS Setup
October 2023

## Slide 22: Making a Capillary – Electronic Discharge Machining
Spools with different ID’s Over 2km (1.25mi) total
Cut from Spool using pliers
Result
Remove ends with EDM Wire Cutting
Flattened ends…
because of pliers (right side)

## Slide 23: Measurement – Example in Practise
4 Installed capillaries
Connector used in the Capillary Open System does not affect the capillary in any way: No deformation No welding/brazing
Design by Fernando Albela Perea

## Slide 24: Measurement – SCADA Data Acquisition
Operation and Data Acquisition through SCADA
Important: Always ensure stable conditions on inlet and outlet of the capillary.
After which, data is recorded for 5 minutes and averaged.

## Slide 25: Measurement – Example in Practise
First measurements compared to theory from earlier:

## Slide 26: Measurement – Example in Practise
First measurements compared to theory from earlier:

## Slide 27: Measurement – Consistency in larger batches
A batch of 8 capillaries, what consistency are we measuring?
Calculation based on measurements at Micro-lab.

## Slide 28: Measurement – Example in Practise
Performance of the Theoretical prediction when compared to measured data
Result: +-5% Still acceptable for flow distribution inside the detector

## Slide 29: Capillary Tested – Now what?
Capillary is done, and ready for installation in the detector system:
Vacuum Brazing of end connections
Installation and routing into the detector
Future:
We are currently waiting for the detector teams to give us the final pressure drops of the evaporators, after this we can size the capillaries accordingly…

## Slide 30: The End Thank you for your attention
Thank you to all the contributors of the project: Derek Jan LANGEDIJK(a), Joao NOITE(a), Liam COOPER(b), Leonid HLUSHENKO(a), Szymon MLECZKO(a), Karol GORNY(a), Martin MACHAC(a), Szymon GALUSZKA(a), Aleksandra ONUFRENA(a), Michal ZIMNY(a), Loic DAVOINE(a), Lukasz ZWALINSKI(a), Jerome DAGUIN(a), Bart VERLAAT(a)
(a) CERN, Geneva, 1211, Switzerland, derek.jan.langedijk@cern.ch (b) STFC, Polaris House, North Star Avenue, Swindon, SN2 1SZ, United Kingdom

## Slide 32: Measurement – Example in Practise
First measurements compared to theory from earlier:

## Slide 33: Capillaries in CO2 Cooling – Why?
Pressure drop for triggering of boiling?  Orifice or Expansion Valve…
Transport & Pressure drop?  Capillary!

## Slide 34: Measurement – More Data

## Slide 35: Measurement – More Data

## Slide 36: Testing and Cutting – EDM Wire Cutting
Normal cut/saw
Burs
Uneven surface
Deformation
Electronic Discharge Machining
Precise cut
No burs
No deformation
Square surfaces
We are planning on bundling a capillary set with (roughly) the same length to cut 100s at a time, saving us costly time in the Main Workshop.
The principle of Wire EDM

## Slide 37: Back-up – BTL Measurements

## Slide 38: Theoretical Prediction – Why is it still so difficult?
Inconsistencies in capillary manufacturing tolerances