## Slide 1: April 10 2024 INFN CNAF TIER1 Update State of the new Datacenter CNAF-CERN DCI Preproduction S.Zani

## Slide 2: New Datacenter state of art
INFN
CINECA
B5
C2
ECMWF
B5 Building OK
New Datacenter at Technopole
2,4km walking distance
7 km far fiber path
CURRENT
DATACENTER
(Viale Berti Pichat)
NEW DATACENTER
(Via Stalingrado)

## Slide 3: Areas of the new Datacenter
High Density
And
Expansion
AREA
INFN DC
Building
B5
CINECA DC
Building
C2
FARMING
TAPE
LIBRARY
NETWORK
LOW Density Computing
AREA
High Density
Expansion
AREA
NOC
SOC
MEETING
ROOM
LEONARDO
“Temperate” water (36°C inlet) for DLC and cold water for Air Cooling
Up to 80kw/Rack
Cold water (26°C inlet) only for Air cooling (Cold isle) system (Up to 16 kW/Rack)
CNAF-Leonardo
Direct cabling connection <100m
100m
30m
FARMING / STORAGE
Resources
Dragon Fly
IB
CORE-1
A7812
OPN/ONE
Skyway
Skyway
LEONARDO
IB
IB
IB
IB
IB
16x100Gb Ethernet
CORE-2
A-7812
FARMING / STORAGE
Resources

## Slide 4: Cabling
The Cabling system is concentrated from every row in the Network Room (Close to center of the building)
LC-LC MM (OM5) 1-100Gb Ethernet
LC-LC SM->1-400Gb Longer distance and 400G-FR4 Ethernet
MPO-12 MM (OM5) 40G-SR4, 100G-SR4, 400G-SR4.2 Ethernet
MPO-12 SM 400G Ethernet (400G-DR4)
RJ45 1-10Gbps
Cabling complete!

## Slide 5: Low density Area
150 racks in place
Under Floor Cooling System operational
First 5 CPU Racks transferred in the new data center In low density area In production
First 64 PB of new storage resources are installed in the new data hall  configuration in progress
First Computing and storage resources

## Slide 6: Network Area
Cabling system from Network Area to every row in place
2x Modular Core Switch/Router (ARISTA 7812) –TIER1 Scientific DC
2x ”Switch/Router” (ARISTA 7280) – General Internet Access
15x Management Switch
2 Racks for GARR POP
Everything in place (Configuration of the devices in progress)
NETWORK ROOM
ONE OF THEN TWO
CORE AND ROUTER RACKS
ARISTA 7812
ARISTA 7280

## Slide 7: High Density and expansion area
Network Cabling racks are in place
The High density farming area can host 3 rows of 16 Racks full of DLC systems (Up to 80 kw/Rack) or very dense air cooled systems (Up to 30kw/Rack)
An Expansion area of about 800 sqm is available for future use
FREE EXPANSION AREA

## Slide 8: Physical connectivity of the building
ECMWF
INFN
CINECA
Fiber access from Via Ferrarese
Differentiated optical fiber accesses are foreseen for network operators from the two sides of the Technopole Area (Via Stalingrado e Via Ferrarese)
At the time of this presentation more than 140 single mode fibers have been installed by Lepida e TIM entering form via Ferrarese.
K2
Fibers in the other way (From Via Stalingrado) will be installed as far as the underground big anti flooding water expansion pool will be finished
Fiber access from Via Stalingrado
(To be done)
Anti flooding
pool
WORK IN PROGRESS
Technopole AREA

## Slide 9: Datacenter Extension Between Current CNAF site and New Technopole site
DCI
1,2Tbps
(3,2Tbps)
Available
INFN DC
(Old site)
2x100G (General IP)
10x100G Ethernet(DCI)
CISCO
Nexus 9516
CISCO
Nexus 9516
C-9500
C-9500
ARISTA
7812
ARISTA
7812
A-7280
A-7280
2x100G (General IP)
10x100G Ethernet(DCI)
INFN DC
(TECHNOPOLE)
vPC
Stackwise
Virtual
Collapsed
IP FABRIC
MUX A
MUX B
MUX A
MUX B
G30-1
G30-2
G30-1
G30-2
Transponders
Transponders
7km

## Slide 10: Tape Area Network Extension
New IBM TS4500
18 Tape Drive
IBM TS1170
FC Switch
FC Switch
FC Switch
SAN 64B-6
FC Switch
SAN 64B-6
TSM – HSM
7 Servers
(old)
IBM TS4500
19 Tape Drive
IBM TS1160
2 Dedicated Dark Fibers (7 km)
Transceiver FC SFP+
FC 32 Gb LWL on SM Fiber (10Km)
Brocade
INFN DC
(TECHNOPOLE)
INFN DC
(Via Berti Pichat
Old site)
Tape data transfer will be done on this extension
Dedicated Dark Fibers are in place
LW 10Km FC Transceivers acquired and installed on Berti Pichat FC Switches
New IBM TS4500 Tape Library and new FC Switches in provisioning phase
1st IBM lib to be relocated at TP
The data migration will continue through the remote SAN, until the Oracle lib will be emptied
TSM – HSM
7 Servers
(new)
Oracle SL8500
- 20 Tape Drive
- 42 PB to be migrated
- To be dismissed

## Slide 11: Conceptual CORE network Configuration
CORE-1
A7812
CORE-2
A-7812
SW/Router-1
SW/Router-2
L2 LACP
Port Channel
General IP
WAN
Underlay: IS-IS
Overlay: VLXLAN BGP EVPN
ESI
FARMING or STORAGE
Resources
OPN/ONE
DC
CORE-1
DC
CORE-2
Router-1
Router-2
ESI
SPINE
SPINE
DC
CORE-3
DC
CORE-4
FARMING or STORAGE
Resources
OTHER
Resources
Possible Scale UP
Evolution
General IP
WAN
OPN/ONE
Collapsed
IP Fabric

## Slide 12: DC Transfer phases
INFN
Nexus 9516
Nexus 9516
Nexus 7018
TIER1
Berti Pichat
LHC OPN/ONE
100Gb/s
100Gb/s
CINECA
TOR
TOR
TOR
TOR
CORE
CORE
TR
TR
DCI 1,2Tb/s
800Gb/1Tb (T1-T1 + T1-WAN)
2x100G (General IP)
LHC OPN/ONE
Nx100Gb/s
Nx100Gb/s
TOR
TOR
TOR
TOR
CORE /
SPINE
CORE /
SPINE
IB/ETH GW
IB/ETH GW
8x100 Gb/s
8x100Gb/s
Leonardo
DCI Between the two Datacenters
Data copy and devices transfer
Swap of the Wide Area Network Routing as far as hardware resources have been moved to the new Datacenter
Decommissioning of the old datacenter
B5
C2

## Slide 13: CERN – CNAF DCI
As presented last year we have a pilot link based on multidomain Spectrum sharing Connection.
We managed to activate a 4x100Gbps to be used as LHCOPN link for INFN-T1 during the Data Challenge 2024
Add/Drop
GEANT Open Line System
ROADM
8x AMP
Milan PoP
Geneva CERN DC
Add/Drop
GARR Open Line System
ROADM
3x AMP
Bologna CNAF DC
TRX
TRX
Nx100 G
or
Nx400 G
Nx100 G
or
Nx400 G
13
1.6 Tbps

## Slide 14: CERN-CNAF DCI (Pre production) Primary and backup path CERN-CNAF
Nexus 9516
Nexus 9516
0
CERN Router1
CERN Router2
2 Transponders
Infinera G30@CNAF
CNAF
CERN
1000 km
2 Transponders
Infinera G30@CERN
Spectrum Sharing (1,6Tbps over 400Ghz)
L3 Overlay
LHC-ONE
LHC-OPN (Backup)
4x100G
4x100G
LHC-OPN traffic on DCI Link 4x100 Gbps
Router GARR
Router GEANT
PRIMARY PATH (as-path: 2038-513)
BACKUP (as-path 2038-137-20965-513
SCS
2x100G
2x100G

## Slide 15: CERN-CNAF DCI
Courtesy GARR
RTT
15 ms
RTT
9.5 ms

## Slide 16: Data Challege 2024 (Using DCI link)
On 400Gbps CNAF-CERN DCI Reached 220 Gbps (5 minute average)
On LHCONE (T1-T2 + T1-T1 per FZK e IN2P3) Reached 145 Gbps
Quite good rates reached (>200Gbps) and network don’t represent a limit for the data movement (Never saturated)

## Slide 17: Telemetry (On transponders)
Data observed via Telemetry on transponder devices (peaks close to 300Gbps)
285 Gbps
Telemetry gives us instant data (not average) and it is better to observe peaks.

## Slide 18: Fiber CUT on DCI (22/3/2024 – 27/3/2024)
OPN CERN – CNAF DCI
OPN-ONE CERN – CNAF (backup)
CUT 22/3/2024
During “CUT time” traffic
Flowed on LHC-ONE “Routed” Path

## Slide 19: CERN-CNAF DCI (Next steps)
DCI on spectrum sharing is ready for production
Pilot activities will continue
400Gbps and multiple 400Gbps Ethernet connections
Extension of the pilot to the new datacenter @Tecnopolo
Try to find a second optical path for redundancy
Improve automation on optical network programmability
Acknowledgments:
GARR Optical : Colantonio, Vuagnin
GARR Packet : Inzerilli, Marletta, Valiante
GARR DC & DevOps : Cesaroni, Chiarelli, Marzulli
CNAF Team: Zani, De Girolamo
CERN Team: Martelli
GEANT Team: SCS Team, Roberts
GARR Management/Amm/CTS

## Slide 20: That’s it

## Slide 21: Backup Slides

## Slide 22: Connection to Leonardo
General IP
WAN
IB
CORE-1
A7812
A-7812
L2 LACP
Port Channel
ESI
FARMING or STORAGE
Resources
OPN/ONE
Syway 1
Syway 2
LEONARDO
IB
IB
IB
IB
Dragon Fly
IB
16x100Gb Ethernet

## Slide 23: Outline
New Datacenter state at Tecnopolo
  Schema, Photos, Numbers
Datacenters Interconnection between the two DCs
  Two ways fiber access to the building
  1Tbps DCI provided by GARR
  Tape Area Network Extension
  Complete plot of the extensions (CINECA, Berti Pichat, Technopole)
Plan for the transfer
  Challenges
New network infrastructure
  Cabling system and technologies used
  Devices HW description
  Description of the collapsed IP Fabric for the CORES
  Leonardo Interconnection
    PoC done last year
    New infrastructure
  Focus on CERN-CNAF DCI
    State of art
      Next steps of the experimentation
    Data Challenge analysis from network point of view
Different kind of workflows and different confidentiality of data (GDPR compliancy and WLCG)
Conclusions