## Slide 1
G. D. Hallewell
Aix Marseille Université, CNRS/IN2P3, CPPM, Marseille, France
1
.
G. Hallewell: Green FCs for Cherenkov detectors and Si tracker cooling: Sustainability session ICHEP2024 Praque 18-24 July 2024
Green use of fluorocarbons in Cherenkov detectors and silicon tracker cooling systems:
challenges and opportunities.
Notes: 1

## Slide 2
“Green” fluorocarbons for Cherenkov detectors & silicon tracker cooling systems: challenges and opportunities
Saturated fluorocarbons (PFCs, SFCs: CnF(2n+2)) chosen for optical properties as Cherenkov radiators: C4F10 & CF4 in COMPASS & LHCb RICH1&2.
Non-conductivity, non-flammability, non-toxicity & radiation resistance
 ideal coolants
- C6F14 used in all LHC experiments,
- C3F8 evaporatively cools ATLAS silicon tracker, TOTEM;
These fluids however have high GWPs (GWP20 > 5000*CO2);
Fluoro-ketones (CnF2nO), while not industrialised over a wide CnF2nO range,
can offer similar performance at very low, or 0 GWP;
Radiation tolerance & thermal performance of 3M NOVEC 649 (lin-C6F12O) sufficiently promising to be considered by CERN to replace C6F14 for cooling,
but acid production and materials compatibility issues to resolve;
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 3: Molecular shapes and GWP (1)
Upper: molecular shapes of SFCs, including common gaseous Cherenkov radiators
Lower: shapes of some non-cyclic CnF2nO analogues
(20-year GWPs noted where known – refs: https://link.springer.com/article/10.1140/epjp/s13360-023-04703-w)
SATURATED FLUOROCARBONS (CnF(2n+2)) with current uses at CERN
FLUOROKETONES (CnF2nO)
COOLING (Liq.)
Toxic
H330
Toxic
RICH
(Gas)
RICH
(Gas (blend))
Probable
Uses
(if/when
available)
COOLING (Liq.)
Si COOLING (Evap.)
RICH (Gas)
RICH (Gas)
Current
uses
at CERN
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
Ex-DELPHI
RICH (Gas)
C2F4O

## Slide 4
Cyclic, non-cyclic & non-cyclic double carbon-bonded C4F8O isomers: refs at end.
Placement of oxygen atom can also determine flammability & toxicity­
Molecular shapes and GWP (2)
High GWP!!
?
ALICE VHMPID,
BTeV studies:
Refractive index,
UV transparancy OK
(similar to C4F10), but…
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

?
?

## Slide 5
From: 2021-22 CERN environmental Report report https://doi.org/10.25325/CERN-Environment-2023-003
R449: (CFH blend) GWP=1397
R1234 (HFO): GWP = 7
NOVEC 649 (C6F12O): GWP=0
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
PFC Loss around 10-12 tonnes
(particle detection and detector cooling)
GWP 23000
GWP 0

## Slide 6
But no mention at all of the ATLAS ultrasonic fluorocarbon leak monitor system !
https://doi.org/10.25325/CERN-Environment-2023-003
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 7
Adding some conclusion here, in case I run out of time:
“Green” fluorocarbons for Cherenkov detectors & silicon tracker cooling systems: challenges & opportunities
Saturated fluorocarbons (SFCs: CnF(2n+2)) chosen for optical properties as Cherenkov radiators: C4F10 & CF4 used in COMPASS & LHCb RICH1&2.
Non-conductivity, non-flammability & radiation resistance  ideal coolants
- C6F14 used in all LHC experiments,
- C3F8 evaporatively cools ATLAS silicon tracker, TOTEM.
These fluids however have high GWPs (GWP20 > 5000*CO2).
While not industrialised over a wide CnF2nO range fluoro-ketones can offer similar performance at very low, or 0 GWP;
Radiation tolerance & thermal performance of 3M NOVEC 649 (lin-C6F12O) sufficiently promising to be considered by CERN to replace C6F14 for cooling;
Cherenkov detectors: subject to optical testing, lin-C4F8O could replace C4F10 while lin-C4F8O or lin-C5F10O blended with N2 and monitored in real time by sound velocity gas analysis - could replace CF4
SI tracker COOLING: Lighter molecules (e.g. C2F4O, with similar thermodynamics to C2F6) - would allow lower temperature, 0GWP operation than evaporative CO2 in Si trackers operated at high luminosity: low order CnF2nO toxicity a problem…
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 8: What gives NOVEC 649/1230 (lin C6F12O: FK-5-1-12) its low GWP?
A: Structure!: a double-bonded oxygen atom on a peripheral spur of the molecule
This fluoro-ketone configuration is:
CF3CF2C(O)CF(CF3)2
8
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 9: What gives NOVEC 649/1230 (lin C6F12O: FK-5-1-12) its low GWP?
Scission by UV photons of l ~300 nm in upper atmosphere (low P, high UV): fragments do not re-associate* into CnF(2n+2) SFCs
*The Environmental Impact of CFC Replacements HFCs and HCFCs
T. WALLINGTON et al Environ.Sci.Technol.1994(28)7 320A https://doi.org/10.1021/es00056a714
https://www.nist.gov/system/files/documents/el/fire_research/R0301570.pdf
9
[15]
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 10: The Cherenkov detector aspect
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 11: The big SFC-using Ring Imaging CHerenkov Detectors at CERN
LHCb RICH 1
(4m3 C4F10)
GWP eqv CO2: 274 tonnes
LHCb RICH 2
(100 m3: CF4 + ~5% CO2)
GWP eqv. CO2: 1737 t
COMPASS RICH
(100 m3 C4F10)
GWP eqv CO2: 6849 tonnes
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
Ideally… replace SFCs with same-order GWP0 FKs with good UV transparency, refractivity…
LHCb RICH 1
(4m3 lin-C4F8O)
GWP eqv. CO2: 0 tonnes
LHCb RICH 2
(100 m3: CF2O + ?)
GWP eqv. CO2: 0 t
COMPASS RICH
(100 m3 lin- C4F8O)
GWP eqv. CO2: 0 tonnes
No! CF2O TOXIC 

## Slide 12
C4F10 (COMPASS: 100m3, LHCb RICH 1: 4m3): GWP20 = 4880,
CF4 (LHCb RICH 2: 100m3): GWP20 = 6870
Cherenkov radiator vessel volume V(m3) filled with
a blend of gases of densities ri (kgm-3),
fractional concentrations wi & individual GWPi (tonnes CO2 eq.)
has a GWP environmental “load” (& release potential) L given by:
) (tonnes CO2 eq.)
Corresponding radiator gas mixture refractivity given by :
)
Can blend small concentration wx of (heavier) SFC or Lin-FK vapour of high
refractivity (n-1)x with wy of light transparent gas (N2, Ar… ) to replicate the
target refractivity (n-1)z of a lighter SFC at high concentration – for lower GWP load.
wx =
V,r
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
Refractive index & GWP ’load’ in a Cherenkov Gas Radiator (vessel only, not including tankage & piping)

## Slide 13
Use real-time speed of sound to get component molar concentrations,wi
(SoS traditionally also called “c” by acousticians to confuse things)
More details (ATLAS system): https://www.mdpi.com/2410-390X/5/1/6
Then use standard refractivity formula to get from calculated w1,2
to refractive index of radiator gas blend in real-time,
then standard relativistic expressions to get from n to Cherenkov g thresholds for different particle species + b = 1 angle
Real-time measurement of speed of sound c takes us via the relative concentrations of the components to the speed of light b and beyond!! in the radiator gas
13
Eyes on the prize…(focus here on LHCb RICH2 (n-1)…)
(488.10-6)CF4 = (~1750.10-6)C5F10O*0.12+(300.10-6)N2*0.88
)
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 14
14
Precision: 10-5 C3F8 into N2 at 1 bar
Chart: CO2 concentration (ppm)
Methodology (ATLAS-developed algorithm) for interpolation of fit parameters for SoS vs. composition)
for ultrasonic analysis of a gas pair of primary interest (e.g. FC/N2) on top of known concentrations of other gases, (e.g. CO2, H2O, O2…)
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
Ultrasonic gas analysis in a process environment with multiple background gases More details: https://www.mdpi.com/2410-390X/5/1/6 :

## Slide 15
Chart: 
| 361.57150866452997 | 256.66370132773199 | 207.76041110631601 | 177.74100163378299 | 156.771959339836 | 140.96541864529999 | 128.432486611158 | 118.12923971441801 | 109.42497216462201 | 101.912772216321 | 95.316482075286103
e thresh | 0.20021 | 0.16566 | 0.14445 | 0.12974 | 0.11878 | 0.11019 | 0.10324 | 0.09746 | 0.092555 | 0.088324 | 0.084626
mu thresh | 4.2043 | 3.4788 | 3.0335 | 2.7246 | 2.4943 | 2.3141 | 2.1681 | 2.0467 | 1.9436 | 1.8548 | 1.7772
pi thresh | 5.4857 | 4.5391 | 3.9579 | 3.555 | 3.2545 | 3.0193 | 2.8288 | 2.6704 | 2.536 | 2.4201 | 2.3188
kthresh | 19.9006 | 16.4666 | 14.3584 | 12.8965 | 11.8065 | 10.9534 | 10.2622 | 9.6876 | 9.1999 | 8.7794 | 8.4119
pthresh | 37.4788 | 31.0115 | 27.0412 | 24.288 | 22.2351 | 20.6285 | 19.3269 | 18.2446 | 17.3262 | 16.5342 | 15.842
% C5F12 | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
C5F12 concentration (%)
LHCb RICH 2 with C5F10O/N2
GWP load = (0.13 molar*1*V.r)
LHCb RICH 2: CF4 thresholds
GWP load = (0.95 molar*4880*V.r)
Cherenkov threshold: lin-C5F10O (eg: 3M NOVEC 5110)/N2
& (heritage) C5F12/N2 blend and GWP load comparison with LHCb RICH2 (CF4: 100m3)
N2-NOVEC5110 (C5F10O) will be very similar (MW 266 vs. 288)
~ 14% molar Novec 5110 gives a GWP load reduction of 1737 tonnes
(everything in the 100m3 radiator vessel):
Even substituting CF4 with ~ 13% molar heritage stock C5F12 SFC (!) reduces GWP load by ~800 tonnes
15
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 16: Radiator volume GWP load: 100 m3 gas radiator with different mw gases blended with nitrogen to replace CF4 (note: blends with Ar very similar: need refractivity data for linear fluoro-ketones, probably similar to SFCs) blends with CO2 not consdered: high CO2 triple point temp (-56 C)  thermodynamic recirculation difficulty)
Chart: Molecular weight of heavy component in N2
| 88 | 288 | 238 | 131 | 84 | 138 | 188
Required Heavy component molar conc (%) in N2 vs molecular weight | 100 | 12.9655 | 17.0909 | 40.4301 | 132.3944 | 37.6 | 18.8
GWP load 100m3 (tonnes CO2) | 1737.28 | 957.5099 | 1170.623 | 0 | 0 | 1737.9585 | 967.448 | 0
CF4 (pure) 1737 tonnes
Krypton: (>100% indicates need
for slight pressuisation)
Xe
CF4
C2F6
C3F8
C4F10
C5F12
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 17
Base fluid | Base fluid density (1bar,25˚C) kgm-3 | Base fluid GWP (20-yr) | Component (n-1) (*106) (@ nm) | % Blend with N2 to match (n-1) CF4 | GWP load (t.CO2) | % Blend with N2 to match (n-1) C4F10 | GWP load (t.CO2)
CF4 LHCb RICH2 (100m3) | 3.56 [18] | 4880 [16] | 488 (180-310 nm) [19] | 100 | 1737 | not applicable | n/a
CF2O | - |  |  | ~100 | 1 | n/a | n/a
C2F6 | 5.63 [18] | 8210 [16] | 793 (180-310 nm) [19] | 38.1 | 1762 | not applicable | n/a
Lin-C2F4O | - |  |  | - |  | n/a | n/a
C3F8 | 7.75 [18] | 6640 [16] | 1180 (250 nm) [16] | 21.4 | 1099 | not applicable | n/a
Lin-C3F6O | - |  |  | - |  | n/a | n/a
C4F10 LHCb RICH1 (4m3): COMPASS (100m3) | 9.97 [18] | 6870 [16] | 1450 (250 nm) [16] | 16.3 | 1119 | 100 | 6849
Lin-C4F8O (Non-cyclic C4F8O)* | 9.5 (est.) | Probably < 1 (NOVEC 5110 Analogy) | 1380 @ 400nm (based on 3M PFG-3480 c-C4F8O [7]: linear C4F8O not yet measured but assumed similar) | 18.4 | 0.18 | 112.7* (>100% would imply necessity of operating C4F8O at slight overpressure) | 1.07
C5F12 | 11.63 [18] (BP 30 ˚C at 1 bar) | 6350 [16] | 1750 (180-310nm)[19] (40 ˚C, undiluted) | 13.0 | 957 | 79.3 | 5857
NOVEC 5110 C5F10O | 10.7 [13] (BP 27 ˚C at 1 bar) | <1 [13] | Not yet measured: probably around 1650 by analogy with C4F10 and C4F8O ratio | 13.9 | 0.149 | 85.2 | 0.91
Table 1: GWP loads of various SFCs and NOVEC 5110 blended with N2 ((n-1) = 310.10-6) to match refractivity of CF4 and C4F10
assumed radiator volume: 100 m3
Positions of presently unavailable-in-bulk CnF2nO fluids are shown in italics. Refractivities to match (CF4 and C4F10) shown in bold.
GWP loads and refractivities calculated using eqs. (1)-(3): assumed radiator volume: 100 m3
*Made in research quantities by Synquest Inc. as isomers Heptafluorobutyryl fluoride PN: 2116-2-07 CAS: 335-42-2
Octafluoro-2-butanone PN: 2117-2-10 CAS: 337-20-2 & Heptafluoroisobutyryl fluoride PN: 2116-2-0A CAS: 677-84-9
https://link.springer.com/article/10.1140/epjp/s13360-023-04703-w
GWP load reduction through CF4 index matching (LHCb RICH2)
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 18
Base fluid | Base fluid density (1bar,25˚C) kgm-3 | Base fluid GWP (20-yr) | Component (n-1) (*106) (@ nm) | % Blend with N2 to match (n-1) CF4 | GWP load (t.CO2) | % Blend with N2 to match (n-1) C4F10 | GWP load (t.CO2)
CF4 LHCb RICH2 (100m3) | 3.56 [18] | 4880 [16] | 488 (180-310 nm) [19] | 100 | 1737 | not applicable | n/a
CF2O | - |  |  | ~100 | 0 | n/a | n/a
C2F6 | 5.63 [18] | 8210 [16] | 793 (180-310 nm) [19] | 38.1 | 1762 | not applicable | n/a
Lin-C2F4O | - |  |  | - |  | n/a | n/a
C3F8 | 7.75 [18] | 6640 [16] | 1180 (250 nm) [16] | 21.4 | 1099 | not applicable | n/a
Lin-C3F6O | - |  |  | - |  | n/a | n/a
C4F10 LHCb RICH1 (4m3): COMPASS (100m3) | 9.97 [18] | 6870 [16] | 1450 (250 nm) [16] | 16.3 | 1119 | 100 | 6849
Lin-C4F8O (Non-cyclic C4F8O)* | 9.5 (est.) | Probably < 1 (NOVEC 5110 Analogy) | 1380 @ 400nm (based on 3M PFG-3480 c-C4F8O [7]: linear C4F8O not yet measured but assumed similar) | 18.4 | 0.18 | 112.7* (>100% would imply necessity of operating C4F8O at slight overpressure) | 1.07
C5F12 | 11.63 [18] (BP 30 ˚C at 1 bar) | 6350 [16] | 1750 (180-310nm)[19] (40 ˚C, undiluted) | 13.0 | 957 | 79.3 | 5857
NOVEC 5110 C5F10O | 10.7 [13] (BP 27 ˚C at 1 bar) | <1 [13] | Not yet measured: probably around 1650 by analogy with C4F10 and C4F8O ratio | 13.9 | 0.149 | 85.2 | 0.91
Table 1: GWP loads of various SFCs and NOVEC 5110 blended with N2 ((n-1) = 310.10-6) to match refractivity of CF4 and C4F10
assumed radiator volume: 100 m3
Even bigger GWP load reduction through C4F10 index matching
(eg here: COMPASS RICH)
G. Hallewell: DRD4 WG 2 Low GWP FC radiator gases: June 19 2024

## Slide 19: CnF2nO fluid selection search criteria
Start(ed)
Non-toxic
(MSDS)
?
N
Y
Non-
Flammable
(MSDS)
?
N
Y
Non-
Oxone-
depleting
?
N
Y
Next CnF2nO fluid
(order & isomer)
to evaluate
Materials/
purifier
Compatible
?
N
Y
N
Y
Rad.
Tolerant
(more for
cooling)
?
N
Y
Dielectric
?
Acid
formation
with H2O
?
N
Y
N
Y
N
Recirc.
Thermo-
dynamics
OK
?
Y
Y
Y
UV-Vis
transparency
OK
?
(n-1) &
Chrom. Disp.
OK
?
N
N
Accept
fluid
Optotests
Materials tests
Bibliographic
Low GWP!
?
N
Y
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 20: Some molecular shapes to study (or eliminate) for UVT, GWP, radiation stability & materials compatibility: example: C4F8O isomers,
Octafluorotetrahydrofuran
CAS: 773-14-8
H332 asphyxiant hazard
Octafluoro-3-methoxyprop-1-ene
CAS: 67641-44-5
H332 Inhalation toxicity Cat. 4
BTeV, ALICE VHMPID evaluated; good properties but high GWP
Pentafluoroethyl trifluorovinyl ether CAS: 10493-43-3
Flammable,
H332 Inhalation toxicity Cat 4
Octafluoro-2-butanone
CAS: 337-20-2
Inhalation toxicity H335:
may cause resp. irritation
2,2,3,3,4,4,4-Heptafluorobutanoyl
Fluoride CAS: 335-42-2
H331 Inhalation toxicity Cat. 3
Heptafluoroisobutyryl
Fluoride CAS: 677-84-9
H331 Inhalation toxicity Cat. 3
Source: https://www.synquestlabs.com
Most promising candidate?
analogy with NOVEC 5110,
649 structures…
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 21
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
UV transparency, refractivity, cmhemical stability & compatibility studies needed
for different CnF2nO molecular shapes. RICH detector community very competent & equipped for detailed UVT & (n-1) - much ex-DELPHI RICH diagnostic equipment at CERN for example
Minuteman Model 302 VM.
Most probable PC spectral range
in new build gas RICH detectors
A
ALICE VHMPID: transparancy
measurements in c-C4F8O
Octafluorotetrahydrofuran
CAS: 773-14-8
Synquest Inc. FL, USA

## Slide 22
The uncertain ECHA (European Chemicals Agency) route to fluorocarbon (PFC, PFAS…) prohibition
(Other people here will talk about this...Path paved with impracticalities?)
Au revoir 3M… need to clarify manufacturers’ attitudes (Dehon Co. (Fr), Synquest (USA), F2 (UK), various companies in China)…
on future lin-fluoroketone (CnF2nO) production
Electronics industry is the driver: we just ride the coat-tails!
.
[51] ECHA/NR/23/04;
https://echa.europa.eu/-/echa-publishes-pfas-restriction-proposal]
[52] ECHA Candidate List of substances of very high concern for Authorisation;
https://echa.europa.eu/candidate-list-table
[53] Annex to the Annex XV restriction report proposal for restriction: Per- & polyfluoroalkyl substances (PFASs); ECHA; 22/03/2023
https://echa.europa.eu/documents/10162/d2f7fce1-b089-c4fd-1101-2601f53a07d1
[54] Per- and polyfluoroalkyl substances (PFAS); ECHA
https://echa.europa.eu/hot-topics/perfluoroalkyl-chemicals-pfas
On the turning away…
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 23: The Silicon tracker cooling aspect See also https://link.springer.com/article/10.1140/epjp/s13360-023-04703-w
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 24: Examples from cooling particle physics Si trackers (ATLAS, CMS, LHCb)
Two distinct types of detector cooling geometry at HL-LHC:
Tube and block ‘DNA’
ATLAS barrel SCT (present) ATLAS ITK Barrel longerons and Si module
block attachment (future HL-LHC)
Disadvantages: long(er) heat conduction path (more interfaces) Si cold(er) coolant: lower Thermal figures of merit NEED COLDER COOLANT!
(2) Micro-channel cooling
LHCb VELO upgrade
Advantages: shortest heat conduction path to coolant: coolant can be warmer:
Disadvantages: fraglity issues: channels etched in silicon and cover plate attached
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
Thermal Figure of Merit (TFM):
  Expressed in terms of temperature difference between Si
  modules & coolant at given power density (units: °C cm2 W−1)
  TFM = ((T(Si module) −T(Coolant)) / (Si module power/cm2)).
  Lower numeric value  better thermal performance.
  TFMs < 4 typical in microchannel devices,
  ~ 20+ in some tube & block geometries.

## Slide 25
Micro-channel cooling: the LHCb VELO upgrade
Recent mastery of evaporative CO2 cooling in microchannels
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 26
CO2 Evaportive cooling problems:
High triple point temperature of -56 °C
CO2 cooling already known to be inefficient at coolant temperatures below -40 °C:
limits the lowest temperature attainable in the tubes of a tube & block cooling system: CO2 cooling now admitted to be insufficient for protection against
radiation damage and protection against leakage current-generated
thermal runaway over the whole HL-LHC envelope (2029-41):
ATLAS plans to change its inner pixel detector half way through…
A very complicated alternative trans-critical krypton evaporative cycle has been proposed
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
see: L. Contiero et al; Cold Krypton system for the Phase III Upgrade of the LHC,
Forum on Tracking Detector Mechanics 2023, Tuebingen Germany May 31-June 2 2023

## Slide 27
Si tracker evaporative coolingome Thermodynamic comparisons: SFCs, CO2, Xe
(F-K thermodynamics would be similar to same carbon order SFCs)
C3F8 won’t go cold enough for HL-LHC operation, particularly in tube & block trackers
C2F4O would have been the ideal fluid: much cheaper than Xe, but toxic…
blend C2F6 with C3F6O?? (C2F6 / C3F8 zeotropic blends already demonstrated…)
R. Bates et al; 2015 JINST 10 P03027
https://link.springer.com/article/10.1140/epjp/s13360-023-04703-w
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 28
The uncertain ECHA (European Chemicals Agency) route to fluorocarbon (PFC, PFAS…) prohibition
(Other people here will talk about this...Path paved with impracticalities?)
Au revoir 3M… need to clarify manufacturers’ attitudes (Dehon Co. (Fr), Synquest (USA), F2 (UK), various companies in China)…
on future lin-fluoroketone (CnF2nO) production
Electronics industry is the driver: we just ride the coat-tails!
.
[51] ECHA/NR/23/04;
https://echa.europa.eu/-/echa-publishes-pfas-restriction-proposal]
[52] ECHA Candidate List of substances of very high concern for Authorisation;
https://echa.europa.eu/candidate-list-table
[53] Annex to the Annex XV restriction report proposal for restriction: Per- & polyfluoroalkyl substances (PFASs); ECHA; 22/03/2023
https://echa.europa.eu/documents/10162/d2f7fce1-b089-c4fd-1101-2601f53a07d1
[54] Per- and polyfluoroalkyl substances (PFAS); ECHA
https://echa.europa.eu/hot-topics/perfluoroalkyl-chemicals-pfas
On the turning away…
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 29
Anyway… thanks for watching and listening:
(some references and back-up material follow
for those interested in this subject)
Also see: https://link.springer.com/article/10.1140/epjp/s13360-023-04703-w
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
Conclusion
(Also at beginning as I didn’t think I’d get this far…)

## Slide 30
Conclusion
Saturated fluorocarbons (SFCs: CnF(2n+2)) are chosen for their optical properties as Cherenkov radiators, with C4F10 and CF4 used in COMPASS & LHCb RICH1&2.
Non-conductivity, non-flammability & radiation resistance  ideal coolants with C6F14 used in all LHC experiments, while C3F8 evaporatively cools the ATLAS silicon tracker and TOTEM.
These fluids however have high GWPs (GWP20 > 5000*CO2).
While not industrialised over a wide CnF2nO range fluoro-ketones can offer similar performance at very low, or 0 GWP;
Radiation tolerance & thermal performance of 3M NOVEC 649 (lin-C6F12O) sufficiently promising to be considered by CERN to replace C6F14 for cooling;
Cherenkov detectors: subject to optical testing, lin-C4F8O could replace C4F10 while lin-C4F8O or lin-C5F10O blended with N2 and monitored in real time by sound velocity gas analysis - could replace CF4 in RICH radiators;
SI tracker COOLING: Lighter molecules (e.g. C2F4O, with similar thermodynamics to C2F6) - would allow lower temperature, 0GWP operation than evaporative CO2 in Si trackers operated at high luminosity: low order CnF2nO toxicity a problem…
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 31: References and back-up material
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 32
Approaches to low-GWP fluorocarbon RICH radiator gases
.
See also:
https://link.springer.com/article/10.1140/epjp/s13360-023-04703-w (paper: EuroPhysics J. Plus, Dec 2023)
https://indico.cern.ch/event/1263731/contributions/5398511/attachments/2648319/4584649
/G_Hallewell_DRD4%20Rad%20Gas%20GWP%20with%20annexes%20May%2016%202023.pdf
https://indico.cern.ch/event/1410802/ (DRD4 WG2 meeting 17 May 2024)
https://indico.cern.ch/event/1420840/ (DRD4 WP_3.1 meeting 28 May 2024)
“From the Speed of Sound to the Speed of Light: and beyond!”
32
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024
Notes: 32

## Slide 33
Cherenkov radiator and related general references (1 of 2) from
https://link.springer.com/article/10.1140/epjp/s13360-023-04703-w
[1] CERN Environment Report 2017–2018 https://doi.org/10.25325/CERN-Environment-2020-001
[2] B. Mandelli; Eco-gas mixtures and mitigation procedures for Green-house Gases (GHGs);
ECFA Detector R&D Road-map Symposium: T.F. 1 Gaseous Detectors, 29/4/2021
https://indico.cern.ch/event/999799/contributions/4204191/attachments/2236047/3789965/BMandelli_ECFA.pdf,
[3] B. Mandelli; R&D for the optimization of the use of greenhouse gases in particle detector systems;
Mini workshop on gas transport parameters for present and future generation of experiments: CERN April 22, 2021
https://indico.cern.ch/event/1022051/contributions/4325947/
[4] G. Rigoletti; Studies to reduce greenhouse gas emissions from detectors at the LHC; EP-DT Seminar May 4, 2022.pdf (cern.ch)
[5] S. Dalla Torre et al; Long term experience with C4F10 in COMPASS RICH-1; Presentation 11th Intl. Workshop on Ring Imaging Cherenkov detectors, Edinburgh, Scotland, Sept 12-16 2022. https://indico.cern.ch/event/1094055/contributions/4932286/attachments/2508724/4311387/RICH2022_C4F10_dallatorre.pdf
[6] 3M PFG-3480: c-octofluorotetrahydrofuran (C4F8O). Note: fluid out of production : product reference now used for a non-fluidic product. For historic product data sheet mentioning its high GWP see (for example): http://static6.arrow.com/aropdfconversion/a7116f41dfdd5b79d2eb7b40afd687f8af23d8ef/mediawebserver(563).pdf
[7] M. Artuso et al; Nucl. Instr & Meth. A Volume 558, (2006), 373-387
[8] Product #2H07-2-08 Synonyms: 2,2,3,3,4,4,5,5-octafluorotetrahydrofuran, Perfluorotetrahydrofuran; CAS No: 773-14-8, MDL No. MFCD00465561: SynQuest Labs Inc., 13201 Rachael Boulevard, Alachua, FL 32615, USA https://www.synquestlabs.com/Home/ProductDetail?SearchText=Octafluorotetrahydrofuran
[9] T. Acconcia et al ; Nucl. Instr & Meth A 767 (2014) 50–60
[10] M. Vollmer et al; Abundances, emissions, and loss processes of the long-lived and potent greenhouse gas octafluorooxolane (octafluorotetrahydrofuran, c-C4F8O) in the atmosphere; Atmos. Chem. Phys., 19, 3481–3492, 2019
[11] 3M Novec® range of fluorinated fluids; https://www.3m.com/3M/en_US/p/c/b/novec/?Ntt=novec
[12] 3M Novec 649/1230 fluid (C6F12O); https://multimedia.3m.com/mws/media/569865O/3m-novec-engineered-fluid-649.pdf,
https://multimedia.3m.com/mws/media/124688O/3m-novec-1230-fire-protection-fluid.pdf]
[13] 3M Novec 5110 fluid (C5F10O); https://multimedia.3m.com/mws/media/1132123O/3m-novec-5110-insulating-gas.pdf
[14] CERN report EN-CV 22/12/2017, EDMS 1751219 2017-334 rev 1.0: Technical Note NOVEC Fluids Qualification Report: Report on the study executed for the qualification of the NOVEC Fluid for Detector Cooling applications.
[15] J. Owens, Understanding the stability and environmental characteristics of a sustainable Halon alternative.
3M Performance Materials 3M Center, St. Paul, MN 55144
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 34
Cherenkov radiator and related general references (2 of 2) from
https://link.springer.com/article/10.1140/epjp/s13360-023-04703-w
[16] CERN Mini-workshop on gas transport parameters for present and future generation of experiments 20/04/2021;
S. Easo; LHCb-RICH detectors and their gas radiators
https://indico.cern.ch/event/1022051/contributions/4333562/attachments/2231064/3780374/LHCb-RICH-Current-GasRadiators-April-2021.pdf,
Options for alternate radiators in LHCb-RICH system (including calculations by O. Ullaland); S. Easo,
https://indico.cern.ch/event/1022051/contributions/4319538/attachments/2231436/3781060/LHCb-RICH-Future-Radiators.pdf
[17] S.Easo; Nucl.Inst.& Meth. A 876 (2017) 168-173
[18] E. Lemmon, M. Huber, & M. McLinden; REFPROP Standard reference database 23, version 9.0 (2010)
U.S. National Institute of Standards & Technology.
[19] E. Nappi and J. Seguinot Rivista del Nuovo Cimento Vol. 28, N. 8-9 2005 DOI 10.1393/ncr/i2006-10004-6
[20] K. Abe et al. ; IEEE Trans. Nucl. Sci. 45 (1998) 648 SLAC-PUB-7705 DOI: 10.1109/23.6826 [21] G. Hallewell et al; Nucl. Instr. & Meth A264 (1988) 219-234
[22] G. Hallewell; Nucl. Instr & Meth A 876, (2017) 50-53
[23] G. Hallewell et al; MDPI Instruments (2021) 5(1), 6;
[24] P. Stassi et al; Ultrasonic Gas mixture analysis system in the Forward RICH of DELPHI,
DELPHI Internal Note 95-124 RICH73, 25 July 1995
[25] M.Sannino; Nucl. Instr. and Methods in Physics Research A 595 (2008) 208–211
[26] C. D'Ambrosio et al; Monitoring, Alignment and Control of the RICH Detectors; LHCb-Memo-2000-80 RICH 6 September 2000.
[27] P. Fauland, PhD thesis; (COMPASS experiment) University of Bielefeld March 2004.
[28] Now marketed as SensComp model 600 transducer, http://www.senscomp.com/ultrasonic-sensors/
[29] T. Blake et al; Nucl. Instr. Meth A791 (2015) 27-31
[30] A. Papanestis; Nucl. Instr. Meth. A766 (2014) 14–18
[31] R. Calabrese et al; 2022 JINST 17 P07013
[32] J. Vavra (SLAC National Laboratory); private communication.
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 35
[33] P. Tropea; The CMS tracker fluorocarbon cooling system,
Engineering Forum: experiences from cooling systems for LHC detectors Oct 30 2008
[34] G. Aglieri Rinella et al, 2019 JINST 14 P07010
[35] G. Anelli et al ; 2008 JINST 3 S08007
[36] D. Attree et al, 2008 JINST 3 P07003
[37] W. Adam et al ; 2021JINST16P02027 CMS Technical Design Report; Pixel Detector Upgrade CMS-TDR-011, CERN-LHCC-2012-016 07/09/2012
[38] ATLAS Insertable B-Layer Technical Design Report; CERN-LHCC-2010-013 ATLAS TDR 19 15/09/2010
[39] O. de Aguiar Francisco et al; Nucl. Instr. Meth A. 1039 (2022) 166874
https://www.sciencedirect.com/science/article/pii/S0168900222003394
[40] Fluoroketone C2F5C(O)CF(CF3)2 as a Heat Transfer Fluid for Passive and Pumped 2-Phase Applications; P. Tuma, 3M Co., 3M Center, 236-2B-01St. Paul, MN 55144, USA, Proc. 2008 IEEE 24th IEEE Semiconductor Thermal
Measurement and Management Symposium, San Jose CA, March 16-20 DOI: 10.1109/STHERM.2008.4509386
also accessible via: https://twiki.cern.ch/twiki/pub/LHCb/SciFiDemoCooling/F.Tuma_c6K_as.....pdf
[41] L. Gruber et al; Nucl. Instr. & Meth. 958 (2020) 162025 https://www.sciencedirect.com/science/article/abs/pii/S016890021930422X?via%3Dihub
[42] ”Building the future of LHCb”; C. Frei, S. Gambetta, B. Leverington; CERN Courier, September 2021 (2 September 2021)
https://cerncourier.com/a/building-the-future-of-lhcb
[43] M. Battistin et al; Int. J. Chemical Reactor Engineering 2015; 13(4): 511–521
[44] R. Bates et al; 2015 JINST 10 P03027
[45] https://lhc-commissioning.web.cern.ch/schedule/LHC-long-term.htm
[46] L. Contiero et al; Cold Krypton system for the Phase III Upgrade of the LHC,
Forum on Tracking Detector Mechanics 2023, Tuebingen Germany May 31-June 2 2023
[47] L. Contiero et al; Krypton, applied as refrigerant for cooling of silicon detector trackers;
GL 2022: 15th IIR-Gustav Lorentzen Conference on Natural Refrigerants, Trondheim, Norway, June 13-15 2023
[48] D. Alvarez et al: Thermo-Mechanical Performance of the Local Supports for the ATLAS ITk Pixel Outer Barrel:
Experimental and FEA Studies; Forum on Tracking Detector Mechanics 2023, Tuebingen Germany May 31-June 2 2023
[49] B. Verlaat; CO2 cooling experiences in the LHCb Velo Thermal Control System
Engineering Forum: experiences from cooling systems for LHC detectors Oct 30 2008
[50] R. Bates et al; 2013 JINST 8 P02006
[51] ECHA/NR/23/04; https://echa.europa.eu/-/echa-publishes-pfas-restriction-proposal]
[52] ECHA Candidate List of substances of very high concern for Authorisation; https://echa.europa.eu/candidate-list-table
[53] Annex to the Annex XV restriction report proposal for restriction: Per- & polyfluoroalkyl substances (PFASs);
ECHA; 22/03/2023 https://echa.europa.eu/documents/10162/d2f7fce1-b089-c4fd-1101-2601f53a07d1
[54] Per- and polyfluoroalkyl substances (PFAS); ECHA https://echa.europa.eu/hot-topics/perfluoroalkyl-chemicals-pfas
Silicon tracker cooling and related general references FROM
https://link.springer.com/article/10.1140/epjp/s13360-023-04703-w
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 36
Strengths CO2 Non-flammable, non-toxic, electrical insulator, non-ozone-depleting, radiation resistant, GWP=1 | Weaknesses CO2 High pressure circulation (60 bar) at ambient temp before cooldown to operating temp High triple point ( -56°C)
Threats CO2 High triple point may make Si tracker operation problematic: less thermal ‘headroom’ after heavy irradiaton (‘thermal runaway’ phenomenon) | Opportunities CO2 Extensive R&D program at CERN Evaporative coolant of choice for ATLAS, CMS for start of HL-LHC program
Strengths C2F6 Non-flammable, non-toxic, electrical insulator, non-ozone-depleting, radiation resistant | Weaknesses C2F6 Very high GWP (around 6000 x CO2)
Threats C2F6 Production will be phased out unless a strong motivation from semiconductor manufacture industry | Opportunities C2F6 Proved to decrease the operating temp of an ATLAS SCT thermal model in blend with 75% C3F8
Strengths xenon Non-flammable, non-toxic, electrical insulator, non-ozone-depleting, radiation resistant, GWP=0 | Weaknesses xenon High pressure circulation (50 bar) at ambient temp before cooldown to operating temp (amost transcritical) Extremely expensive
Threats xenon Very difficult future procurement (war in Ukraine) (10-8 atmospheric content.) | Opportunities xenon Could find expertise In particle physics community for fabrication of circulators: already used in dark matter experiments
Strengths CnF2nO Non-flammable, non-toxic, electrical insulator, non-ozone-depleting, radiation resistant, GWP=0 | Weaknesses CnF2nO
Threats CnF2nO Large scale industrial production may depend on the phasing-out of SFCs, needs of semiconductor manufacture industry: Material compatibility needs further study. | Opportunities CnF2nO Expertise in particle physics community for 3M NOVEC 649 (C6F12O)
(5.7) SWOT analysis of cooling fluids HL-LHC
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 37
The uncertain ECHA path to prohibition
(a path paved with impracticalities?)
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 38
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 39
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 40
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024

## Slide 41
G. Hallewell: Green FCs for Cherenkov detectors & Si tracker cooling Sustainability session: ICHEP2024 Prague 18-24 July 2024