## Slide 1: The new Prévessin Data Centre (PDC) at CERN
2024 CERN openlab Technical Workshop
L. Atzori, W. Salter, O. Barring & E. Bonfillou – March 26th, 2024

## Slide 2: Agenda
Project goal and timelines
Organization and roles
Architecture overview
IT rooms
Cooling and heat recovery
Monitoring dashboard of one IT room
Conclusion

## Slide 3: Project goal and timelines
PDC needed to provide computing needs of HL-LHC, which are expected to be ten times higher than today
PDC hosts servers for physics data processing and “business continuity / disaster recovery” infrastructure
MDC (Meyrin Data Centre) will continue to run in parallel, with a particular focus on data storage

## Slide 4: Organization and roles
The approach has been for a turn-key DC solution:
→ Based on functional specifications
→ Including 10-years operation and maintenance
The project follows the FIDIC Gold Book standard for project design, build and operation
CERN specific exceptions to the above:
→ EN-EL is responsible for the provision and maintenance of the HV systems
→ EN-AA is responsible for the operation and maintenance of the safety systems (smoke detection and evacuation, video surveillance and access control)

## Slide 5: Architecture overview
Total power of 12 MW:
→ 4 MW per floor
→ 1st phase (now) has 2nd floor only
→ 2nd phase (HL-LHC) will add 1st floor
→ 3rd phase will add ground floor
Total of 6 IT rooms:
→ 2 per floor
→ 2 MW per room
90 racks per IT room:
→ 78 server racks
→ 12 network racks
Ground print of 2,250 m2:
→ 70m * 37m * 19m
Total surface of 6,400 m2:
→ 2,100 m2 for IT rooms
Located in front of the CERN Control Centre (CCC)

## Slide 6: IT rooms (1)
Each room contains:
→ 1 network pod (center)
→ 4 server pods
Pods are powered by two separate feeds:
→ 1 without UPS
(25kW/rack)
→ 1 with partial UPS coverage
(20%, 12kW/rack)
Non-UPS racks are for batch workers
UPS racks are for BCDR and services
UPS covers for micro-cuts ( <~ 15 seconds)
After that, covers only for clean automated shutdown of connected capacity
→ UPS is not designed to cover for extended outages! ←

## Slide 7: IT rooms (2)
Rear view of a rack:
→ Hot air inside pod
→ 1 PDU per feed
→ IPMI (green)
→ Data (white)
Front of servers facing outside pod

## Slide 8: Cooling and heat recovery (1)
For 1st phase: 4 * 2 MW Jaeggi dry coolers on the roof
→ N+1 redundancy
→ 1 for technical areas (non-IT rooms)
For each new phase:
→ 2 * 2 MW additional dry coolers to be installed
→ All piping work already done
Starting from 20ºC outside temperature:
→ Dry coolers in adiabatic mode with water recycling
to improve WUE
→ PDC designed for a PUE target of 1.1 (max 1.15 contractually) ←

## Slide 9: Cooling and heat recovery (2)
One 2MW dry-cooler on a truck
Two 2MW dry-coolers on the roof

## Slide 10: Cooling and heat recovery (3)
Each IT room is equipped with large fan-walls:
→ 5 * 500kW fan-walls made by Schneider
→ fan-walls operate in N+1 redundancy mode
→ largest fan-walls in Europe
Air circulates in a closed loop
Inlet temperature:
→ 25ºC on average
→ can go up to 32ºC in hot periods
Air-flow in the IT rooms (lateral view)

## Slide 11: Cooling and heat recovery (4)
One half-fan module being moved
Fan walls being installed

## Slide 12: Cooling and heat recovery (5)
Hot water from IT rooms arrive in the heat recovery room
For 1st phase, 3MW will be transferred to the heating plant via 2 * 1.5 MW water/water heat exchangers
For 2nd phase, 4MW in total will be transferred to the heating plant via one additional water/water heat exchanger of 1MW
This recuperated energy will heat the buildings on the CERN Prévessin site

## Slide 13: Monitoring dashboard of one IT room

## Slide 14: Conclusion
PDC to provide computing capacity for HL-LHC:
→ 1st phase is 4 MW, 2nd phase is 8 MW and 3rd phase is 12 MW
→ Turn-key solution with a 10-years operations and maintenance included
Project carried out on-time with a particular focus on energy efficiency (1.1 < PUE < 1.15)
4MW of energy recuperated to heat CERN buildings on the Prévessin site
PDC powered by two separate power feeds
→ One without UPS
→ One with 20% on UPS coverage
→Technical building, unfortunately no visits are possible←