## Slide 1: Preliminary investigation for the design and implementation of a Rad-Tol analog output peripheral card
Author
Francesco POZIELLO
Supervisor
Nikolaos TRIKOUPIS
TE-CRG-IC
Instrumentation & Control for Cryogenics

## Slide 2: Introduction – Contents
  The purpose of this presentation is to describe the process and all the phases for the development of the R&D peripheral card for the LHCb upgrade for the Long Shutdown 4.
  For Digital Input and Digital Output card, the design has been validated and tested under radiation this fall.
  The “new” R&D card design has started in the beginning of October 2023.
  The selection of radiation tolerant components has been validated by the BE-CEM-EPR section.
  The TE-VSC-ISC section gave support for the output topology.
Figure 1: CERN’s Large Hadron Collider
Figure 2: DI/DO card proposed solution for crate

## Slide 3: Context and goal
  Guaranteed and certified Rad-Tol (Radiation Tolerant) system (CERN standard) for the LHCb (point 8) for LS4.
    Currently, the I/O PLC modules are in the free radiated areas.
    QURA, QURC-A, QURC-B and QUIC.
      ≈ 450 input channels.
      ≈ 80 output channels.
    Pros:
      Input/Output rad-tol card (up to 450 Gy).
      Free space in ULs zones.
      Design control.
      Compliance with cryogenic IC’s CERN new standard.
      3 versions.
Figure 3: EDMS 2311633, Long Term Schedule for CERN’s accelerator complex
Figure 4: Chronology of upgoming events for R&D design for DIOT from CRG-IC

## Slide 4: Context and goal | Current situation
PLC & PLC I/O
(UL84 & UL86)
Figure 6: Point 8 underground scenario. UX85 is the cavern, QURA is in US85. In UL84 and UL86 there are the AI/AO modules
Figure 5: Electrical cabinet current strategy according to EDMS 1970931

## Slide 5: Context and goal | Proposal
(UL84 & UL86)
PLC
UL84/86
UX85
US85
R&D card (Analog and Digital)
Figure 7: Proposed Solution with the DI/OT in LHCb

## Slide 6: Context and goal | Proposal
Figure 8: Proposed Solution from a control system point of view. On the left: The current solution. On the right: the proposed solution with the DI/OT

## Slide 7: Context and goal | Proposal
  The designed cards will be placed inside the DIOT (Distributed Input/Output Tier), which comprises electronics modules near a particle accelerator, controlled by the master in the Front-end tier via a fieldbus.
    Typically feature FPGA-based boards for data sampling, output control, and safety-critical tasks in radiation-exposed or radiation-free areas.
Figure 9: The DI/OT tier from BE-CEM group

## Slide 8: Requirements
  Connectors:
  Female pins to power side
    Safety
  D-SUB type
    Widely used
    Easy buying
    Compact ( more channels)

## Slide 9: Connectors
Figure 10: Front Panel DIOT with D-SUB connectors
15 pins SUB-D connector case: here we will have a maximum of 7 channels (mixed version)
Figure 11: Front Panel DIOT with D-SUB connectors
26 pins SUB-D connector case: here we will have a maximum of 13 channels (mixed version)
Figure 12: Front Panel DIOT with D-SUB connectors
104 pins SUB-D connector case: here we will have a maximum of 52 channels

## Slide 10: RoadMap developments for R&D card
Stage 1
Technical requirement collection for I/Os
Stage 3
Prototype and testing
Stage 2
Design and components selection

## Slide 11: Stage 1: Technical requirement collection for I/Os
  BMX-AMI-0810 isolated analog input module.
  28 ways, 1 connector.
  Analog input type: 4-20 mA and 0 – 10 V.
  Analog input number: 8.
  ADC: 16 bit.
  BMX-AMI-0802 non-isolated analog output module.
  20 ways, 1 connector.
  Analog output type: 4-20 mA.
  Analog output number: 8.
  Resolution: 16 bit.
Figure 14: Schneider new channel isolated BMX AMI 0810 input module
Figure 13: Schneider obsolete not channel isolated TSXAEY1600 input module
Figure 15: Schneider obsolete not channel isolated TSXASY800 output module
Figure 16: Schneider new not channel isolated BMX AMI 0802 output module
Replacement during LS3
Replacement during LS3
Figure 17: Modules which would be placed in the free radiated area

## Slide 12: Stage 1: Reverse engineer of I/Os industrial modules
Figure 19: Top view of BMX AMI 0810 PCB
Figure 20: Bottom view of BMX AMI 0810 PCB
Figure 21: High level block diagram of BMX AMI 0810
Figure 18: Schneider new channel isolated BMX AMI 0810 input module
  Isolation → static multiplexing through optoswitches.
    Between channels ± 300 VDC.
    Between channels and ground ± 1400 VDC.

## Slide 13: Stage 1: Reverse engineer of I/Os industrial modules
Figure 23: Top view of TSXASY800 output module PCB
Figure 24: Top view of TSXASY800 output module, vertical mini-PCB
Figure 25: High level block diagram of TSXASY800 output module
Figure 22: Schneider obsolete not channel isolated TSXASY800 output module
  No isolation.
    Between channels and bus ± 1000 VRMS.
    Between channels and ground ± 1000 VRMS.

## Slide 14: Stage 2: Design and components choice
  Bottom-up approach.
  Radiation Tolerant components.
    RADWG database.
    Cooperation with BE-CEM-EPR section.
  Connectivity.
    SUB-D connector.
  Simple design.
    Minimize the number of active components.
  Tested industrial design.
  DI/OT standards.
    Cooperation with BE-CEM, DIOT project leader.
Figure 26: Components selecting approach for R&D project design

## Slide 15: Stage 2 – Design and components choice
Custom mixed block diagram
DAC: cons
Active component: suffers radiations
Less space
Costs
Figure 27: High level block diagram of the R&D card for LHCb

## Slide 16: Stage 2: Design and components choice
Figure 28: High level design for the R&D card. It is possible to observe that there is no DAC in output, since we will use a VCCS to produce directly the 4-20 mA loop

## Slide 17: Stage 2 – Design | Input side: channel isolation
  Space-channel isolation trade-off
    Channel-to-channel isolation
    No isolation
    Group isolation
  Isolation between different zones into the cavern.
Figure 29: Group isolation between 8 channels
Figure 30: Different zones with group isolation

## Slide 18: Stage 2 – Design | Output side: isolation
IMPORTANT REMARK
The galvanic isolation in output may be made externally.
Figure 31: External galvanic isolation for output (Simon Francois Martin’s credits)

## Slide 19: Stage 2 – Output design
  Our primary goal was to generate a 4-20 mA output using a voltage-controlled current source (VCSS). To minimize the use of active components, we opted for the enhanced version of the Howland Current Pump, which gives in output a fixed current for a certain DC voltage.
Simple
Improved
Figure 32: Howland Current Pump for 4-20 mA standard, simple version
Figure 33: Howland Current Pump for 4-20 mA standard, improved version

## Slide 20: Stage 2 – Output design
FPGA
Low-Pass Filter
Howland Current Pump
VDC
PWM [3.3 V]
4-20 mA
Phoenix Block
Actuators and transmitters
Figure 34: Low-pass filter with unity gain to filter the DC component from PWM signal
Figure 35: PWM signal, in blue the DC component
Output

## Slide 21: Stage 2 – Output design: simulations
  We performed several simulations on LTSpice to test the efficiency of these circuits.
    Best results are achieved from the improved configuration.
    Different radiation tolerant components tested.
    The simulations has been validated from measurements in the laboratory.
Figure 36: LTSpice improved Howland current pump for 4-20 mA
Figure 37: LTSpice simple Howland current pump for 4-20 mA

## Slide 22: Stage 2 – Output design: PCB designing
  Instrumentation for the measurements.
    Power supply for op-amps.
    Function generator for the PWM signal.
      Frequency of 50 kHz for current resolution.
    Digital multimeter for measurements.
Figure 38: Top and Bottom view of the output prototype
Figure 39: 3D view of the PCB prototype
Figure 40: Picture of the PCB during the testing

## Slide 23: Stage 2 – Output design: 4-20 mA testing results
  Results obtained with 5% of resistance tolerances.
Figure 41: Load current vs Duty cycle for output prototype for different loads
Figure 42: Load current vs Duty cycle for output prototype for different loads (zoomed)
Figure 43: Load current vs load resistance for output prototype for a fixed duty cycle (78%)

## Slide 24: Stage 2 – Output design: testing results
Figure 44: Load current vs load resistance for output prototype for fixed duty cycle (78%), with 5% of resistance tolerances
Figure 45: Load current vs load resistance for output prototype for fixed duty cycle, with 0.1% of resistance tolerances

## Slide 25: Stage 2 – Output design: final remarks
  The improved version is necessary if we use resistors with high tolerances.
  The buffer is necessary.
  The improved version requires more supply current from the backplane.
  The tests have been conducted with the operational amplifier OPA192.
    The operational amplifier OPA602 has to be tested.
  The tolerance of feedback resistors must be taken in account.
Figure 44: Results with 5% of resistance tolerances
Figure 45: Results with 0.1% of resistance tolerances

## Slide 26: Stage 3 – R&D prototype
  The project has led to a meeting between the CRG-IC section with other CERN’s sections.
    BE-CEM-EDL: Greg Daniluk (DI/OT project leader).
    BE-CEM-EPR: Salvatore Danzeca (section leader), Raphael Berberat, Salvatore Fiore, Rudy Ferraro.
  An output design for 4-20 mA from TE-VSC-ICM section has been already validated and tested (Nikolaos Chatzigeorgiou).
    It is based on the Howland Current Pump.
    Validated radiation tolerant design (e.g. EDA-03944).
    Tested and used in several designs from the VSC group.
  R&D prototype has been designed and on-going testing.
    Testing of the output design from VSC group for the 4-20 mA.
    Testing of an ADS7852 (ADC) radiation tolerant from EPR section’s advice.
    Testing of a negative charge power supply.
    Testing of general-purpose component measurement circuits.

## Slide 27: Stage 3 – R&D Prototype
Figure 46: Top and Bottom view of R&D prototype

## Slide 28: Stage 3 – R&D Prototype
Figure 47: Picture of the R&D PCB realized

## Slide 29: Stage 3 – Output design from VSC group
  Pros
    4-20 mA transmitter tested and validated.
    Radiation Tolerant.
    Support from VSC group.
    Simple design.
    Howland Current Pump with a BJT.
  Cons
    More components.
    More supply.
Figure 48: 4-20 mA loop transmitter from VSC group (Nikolaos Chatzigeorgiou)

## Slide 30: Stage 3 – Negative Charge Pump
Negative Charge Pump
Negative Power Supply [-VDC]
Figure 49: Negative Charge Pump to produce negative power supply
Positive Power Supply [+VDC]

## Slide 31: Stage 3 – 4-wire resistance measurements
In 4-wire resistance measurements, current is forced through the source terminals (HI, LO). The sense terminals (HISENSE, LOSENSE) are configured for high impedance, and this configuration directs current through the resistance.
We will use the output design from VSC group to produce this current, with a different current span.
Figure 51: 4-wire resistance measurements circuit
Figure 50: Current generator from the VSC group

## Slide 32: Stage 3 – Capacitance measurement circuit
We also added a measuring capacitance circuit, which works just like as a digital multimeter.
The method is based on the rise time measurement.
Measuring the time  Calculate capacitance
Figure 53: Circuit to measure the capacitance
Figure 52: Circuit to measure the capacitance on the R&D prototype

## Slide 33: Conclusions and remarks
The investigation regarding of the custom card is on-going.
  Tests will be made on the R&D prototype PCB to validate the topologies showed.
The output design based on the Howland Current Pump from the VSC group for the 4-20 mA generation is validated and tested under radiations.
This study has been interesting and fascinating, showing all the aspects regarding the radiation tolerance compliance and the hardware design with the best rule of thumbs.
From this work I wrote my Master’s Thesis, graduating with honors at Università degli studi di Napoli ‘Federico II’ and at Politechnika Łódzka on December 2023.
Figure 54: Title page of my MSc’s thesis

## Slide 34: Thanks for your attention!

## Slide 35: Questions?