## Slide 1: Recommendation #5 and cooling water survey
PSB magnets task force day the 14th of December 2023 – S. Deleval – EN-CV
2023-12-14
Reference (https://indico.cern.ch/event/1356657/)

## Slide 2: Recommendation #5
Maintain a high level of awareness of the consequences of accidental pollutions on the magnets in the team carrying out the maintenance of the cooling circuits to reduce the risk of accidental pollution. Interact proactively with EN Coordination and EN-CV link persons to ensure that appropriate awareness is given to all teams intervening in water circuits.
Communication including the Contractors following the task force.
Technical meeting related to water quality and water treatment.
Many actions already in place since LS2 and previous pollution. For example:
  Integration of the past experiences for the technical specifications of the new frame contracts.
  Modification of the PS, SPS and LHC circuits to avoid injection of resins in the circuits (additional modification to be implemented in the coming year)

## Slide 3: Actions
Water analysis with a detection limit decreased from 1,6 ppm to 0,2 ppm
After filtration of the water, analysis of the suspender matter by Automatic Particles Analysis
Samples taking by EN-CV
RP measurement
Analysis performed by an external laboratory (Via CV Water Treatment contract)
Samples taking by EN-CV
RP measurement
Analysis performed by EN-MME

## Slide 4: LHC

## Slide 5: SPS - NA

## Slide 6: CPS

## Slide 8: Summary and plan for future work
Poor brazing interfaces presenting numerous discontinuities
Corrosion selectively attacks Cu at the interface with the Sil-Fos braze (Cu-Ag-P) and the Cu phase within the braze metal
The damage is more severe on samples with longer service time
Also, the S presence in the conduct inner surface increases with the service time
Nevertheless, the same phenomena was observed in sample installed for short period (2 weeks) and HIE-ISOLDE circuit (3 years)
The S origin could be related with ion-exchange resin debris present in the cooling water
The Cu-Ag braze present on PSB samples was not affected at the same level as the Sil-Fos
Erosion-corrosion progressing, but no major reduction of wall thickness observed
Improve brazing quality (soundness, imperfections and geometry – misalignements)
Avoid use of brazing processes/fillers requiring activated fluxes
Avoid sources of S contamination
Monitor regularly and traceably the quality of the water
Regular regeneration of the resins
Dry and inert the circuit during maintenance
Recommendations
ST-2 – A.T. Perez Fontenla & S. Sgobba
Outcome of the PS Booster Magnets Task Force Day presented at the 331st IEFC the 23rd of June

## Slide 9
 |  | Extracted from | Time in service | Material | Sulphur content | Failure
PSB | Sample #1 | PSB main quadrupole | 50 years | Cu/Cu | Up to 5.5 wt. % | At the Sil-Fos interface
 | Sample #2 | PSB main quadrupole | 2 weeks | Cu/Cu | Traces | 
 | Sample #3 | PSB bending dipole | removed LS2 | Cu/Cu & Cu/StSt | Up to 5.5 wt. % | 
 | Sample #4 | PSB main quadrupole | removed YETS 21/22 | Cu/Cu | Up to 5.5 wt. % | 
 | Sample #5 | PSB main quadrupole | removed YETS 22/23 |  |  | 
 | Sample #6 | PSB main quadrupole | removed YETS 22/23 |  |  | 
HIE-ISOLDE | Sample #7 | Conduct | Installed LS2 | Cu-alloy/Cu | Traces | 
Current understanding
ST-2 – A.T. Perez Fontenla & S. Sgobba (EN-MME)
Particles containing “S” are present in the water
Representative number of particles present in suspension within the PSB water were collected in a membrane and analysed by Automatic Particle Analysis (APA)
Apart from “S”, particles rich in other elements were also present: Fe rich ~ 54 %, Ca ~ 12 %, Al ~ 11 % or Cu ~ 6 %
The presence of micrometric “S” rich particles is confirmed (~ 0.82 % of the 15.000 analysed)
What do we know?
Examples of Cu-Ag-P brazed joints presenting similar corrosion were found in papers about transformers and tap water ducts. In those cases, sulphide-containing species in the water was reported as the main cause of the attack
Brazed joints fabricated from a high-Ag filler, that contained no “P”, exhibited no corrosion when exposed to the same sulphide environment
In our samples the “S” presence increases (up to 5.5 wt. %) with operation time but same corrosion phenomena (incipient) in samples with only “S” traces
Is sulfur the root-cause in our cooling circuits failure?
“S” is not detected in the PSB water when analysed by ICP-OES (detection limit 1.6 ppm ) or under the form of SO4-2 by IC-CD (detection limit 0.1 ppm)  Test Dec. 2022
Nonetheless, evidence of “S” contamination at the inner surface of some conducts is confirmed by different techniques (EDS and XPS)