## Slide 1: Design cooling PP1 and cooling pipe integration in SR1
Emiliano Dané
LNF - 20240201

## Slide 2
ITk PP1 piping
16 IN/15 OUT cooling loops per side
Inner System: 3 loops
Outer System: 11 loops
  Outer Barrel: 8 loops
  Outer Endcap: 3 loops
Warm Nose: 2->1 loop
Inner System
Outer Barrel
Warm Nose
Outer Endcap
ITk PP1 PIPING A-side

## Slide 3: Update on piping in PP1
Flex Lines
  New design of the Flex Lines, overall regarding the connection to the Outer PP1 wall
Temp 4w
  No more Temperature sensors in contact with the fluid, but only on the surface
Foot prints
  Aluminum plates are positioned to the BH in order to fix structure for handling the Electrical breakers
Bulkheads bolts inside the envelope
Electrical Breakers
  Big problem in obtainng the quotation
Prototytpe
  Also for the prototype, the company is getting a lot of time to deliver the bent pipes

## Slide 4: Detector's manifolding preparation for the SR1 Assembly

## Slide 5: Inner System

## Slide 6: IS MANIFOLD (side A)
4/6
4/6
4/6
4/6
4/6
8/10
4/6
6/8
6/8
4/6

## Slide 7
PP1 Manifold Assembly Procedure
Step 0
Not clear to me if will be assembled in SR1 or in USA
Pipes from the detector

## Slide 8
Final View
Top View
Closed by fittings+caps in order to perform the pressure tests in SR1, then
romoved.
The use of sleeves is foreseen in order to have 3 shots in case of problems during the assembly in the PIT

## Slide 9: EC Piping Assembly in Production Sites

## Slide 10
Exhaust Manifolds
3D printed
DETECTOR SIDE
EC PP1 MANIFOLD
PP1 SIDE

## Slide 11
The plan is to weld the Inlets and Exhausts manifold just after mating each layer in order to perform the test by CO2 cooling plant and also because would be impossible to weld it after having comlpeted the detector.
In the 3D model I used the Swagelok Orbital Welding. Not yet defined the Welding Machine will be used in Frascati.
Layer 2
Layer 2 EC Inlet manifold welding
Layer 2 EC Exhaust manifold welding
S. Tomassini and D. Orecchini

## Slide 12
EC centina
EC flange
EC PP1 Manifold
EC elbow
welding plane
What about welding back solution: pocket welding is a possibility?
EC Detector Manifold
40mm
For the Polysude is better having the welding plane @20mm while for the Swagelok due to the "wings" should be better a little bit higher
Possible clash between the EC flange and the Swagelok Orbital Head

## Slide 13: Outer PP1 piping Barrel Status

## Slide 14: OB MANIFOLD
Manifold for capillaries
Exhaust Manifold
Inlet Manifold
Cooling Groups defined by colors
Heat Exchanger

## Slide 15
In order to get the minimum number of weldings in SR1, the target is build all the pipes in the workshop, including some parts of the warm nose line.
Red circles are the warm nose joints connecting the two halves (A1 and A2 OB parts). We are thinking to put the whole manifoldings.
All capillaries will be closed by caps (removable without cutting)
A1 part
A2 part
Warm Nose in place and welded

## Slide 16: PP1 Assembly in SR1

## Slide 17
Step 0: Aluminum plates in order to support EB holders

## Slide 18
Step 1: OB piping and manifolds insertion
Step 1.1 Insertion of the Upper part
Step 1.2 Insertion of the bottom part
Step 1.3 Weld the 4 joints of the Warm nose line (slide ...)
OR Insertion of the whole OB+WN piping and also parts of the endcap.

## Slide 19
Step 2: Insertion of the DP boxes and DP capillaries welding

## Slide 20
Step 3: OE and OB detectors insertion. Services on the trolley.
Outer Barrel exhaust pipes
Endcap cooling pipes
All these pipes arrive closed in order to perform the pressure test

## Slide 21
Step 4: PP1 Outer Wall shifting of 150mm in order to weld the OB U-pipes

## Slide 22
Step 4: OB U pipe Welding and Pressure Testing by using temporary pressure lines, with sacrificial VCR

## Slide 23
Step 5: OB U pipe Welding and Testing
The back solution is foreseen done by using the sleeves

## Slide 24
Step 5: OB Welding of the capillaries
Capillary weldings:
79 in total per side
39 A1 part (upper)
40 A2 part (bottom)
Pressure Tests performed by temporary pressure lines
AMI Welding Head

## Slide 25
Step 6: Outer Wall flange back in position

## Slide 26
Step 6: EC pipe welding and test
6 weldings (2 per layer) in order to connect the EC to the VCR

## Slide 27: BACKUP