## Slide 2: LHCb detector upgrade Cryogenics
T. Koettig, C. Fabre, J. Bremer

## Slide 3: Content
Part 1
  General PID of Proximity cryogenics
  Points for discussion – agenda
Part 2
  Cryolab R&D support options
Part 3
  Knowledge database and existing experience

## Slide 4
PID
Surface
Cryoplant

## Slide 5
Surface
Cryoplant
Test facility?
Interface
PID
Questions:
Operation modes
Number of circuits
Max. system pressure
Operational pressure and temperature => n. slide
Interface Proximity cryogenics vs. Detector cryogenics

## Slide 6
Temperature stability vs. time in the N2 supply line
Mass flow rate depending on:
  heat load,
  vapor quality x
  orientation dependency: dp as fct. (x)
  static height difference in circuits
Cooldown and warm-up procedure
…
Two-phase flow nitrogen as a technical coolant

## Slide 7: Testing options at 80 K in the Cryolab

## Slide 8: Cryolab LN2 test infrastructure
Two-phase nitrogen cooled sample environment in vacuum
Pressure test at cold up to 5 bara for feedthroughs, interfaces etc.
Leak test under the same conditions with He to vacuum

## Slide 9: Test stand features
Sample environment at 80 K, actively cooled
Thermal shield actively or passively cooled
Sample He leak test to vacuum up to 5 bara at cold

## Slide 10: Full tests stand, LN2 supply at 78 K from 500 l Dewar

## Slide 11: Pressure Drop and Heat Transfer in Two-phase flow N2
T. Koettig, C. Fabre, J. Bremer

## Slide 12
Content
Two-phase flow pressure drop
Test stand geometry and features
Pressure drop: measurement results in horizontal, vertical up- and downward orientation N2
Verification of the test set-up by starting in subcooled liquid
Summary

## Slide 13
Two-phase Flow Pressure Drop
Void fraction:
Void fraction versus vapor quality
Void fraction versus mass velocity
x↑  ε↑
G↑  ε↑
in kg/(m2s)
Frictional pressure drop:
∆pf
x
1
0.85
= 0
at x ≈ 0.85
Frict. press. drop versus vapor quality
0
0

## Slide 14
Flow pattern map I
Fig.: Flow pattern for horizontal flow
VDI Heat Atlas
Fig.: Flow pattern map according to Taitel and Dukler
VDI Heat Atlas
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 15
Flow pattern map II
Fig.: Flow pattern for vertical flow
VDI Heat Atlas
Fig.: Flow pattern map according to Hewitt and Roberts
VDI Heat Atlas

## Slide 16
Flow pattern map III
From: VDI Waermeatlas Hbb4, 2006
S => SW
Intermitt.
Annular
Dry-out
Mist

## Slide 17
Experimental Set-up
p
h
1
2
3
4
5
6
EH 1
EH 2
Test
Test conditions di=6 mm | 
Pressure (bar abs.) | 2.8
Internal diameter (mm) | 6.0
Mass flow (g/s) | 0.6 – 2.0
Mass velocity (kg/m2s) | 22 - 72
TT
LN2 Dewar
4 bar
Precooler
EH 1
EH 2
EH 3
Joule-Thomson expansion
Sample
FT
PT
1
2
3
4
5
6
PT
TT
Cryostat with thermal shield
LN2
1 bar

## Slide 18
Experimental Set-up
p
h
1
2
3
4
5
6
EH 1
EH 2
Test
TT
LN2 Dewar
4 bar
Precooler
EH 1
EH 2
EH 3
Joule-Thomson expansion
Sample
FT
PT
1
2
3
4
5
6
PT
TT
Cryostat with thermal shield
LN2
1 bar

## Slide 19
Results – Horizontal Orientation
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 20: Results – Horizontal Orientation
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 21: Results – Horizontal Orientation
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 22
Results – Horizontal Orientation
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 23
Vertical Upward Orientation

## Slide 24
Results – Vertical Upward Orientation
Flow is always in chaotic regime
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 25
Vertical Downward Orientation

## Slide 26
Results – Vertical Downward Orientation
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 27: Verification of the set-up
Enter the two-phase range from the liquid phase (subcooled)
Monitor the change in pressure drop
Monitor the temperature behaviour single phase to saturation conditions

## Slide 28
Results – Verification Test
Temperature inlet

## Slide 29
Summary
Two phase flow is special, remember the cooling effect by Δp(G) or Δp(q)!
Pressure drop at x~0.5-0.85 can be much higher than in gas or liquid phase
Deviation in vertical upward orientation of the models for small vapor quality
Models fail to predict pressure drop for vertical downward direction
First bubbles create buoyancy effect that overcomes gravitational influence
Consider the dry out and the sudden decrease in heat transfer for x>~ 0.7
Design for sufficient flow speed to avoid phase separation => syphons/instabilities
Parallel channels => tuning of the inlet restriction to 100 % pressure drop of the heated section

## Slide 30
Thank you for your attention

## Slide 31
Two-phase flow pressure drop
The total pressure drop in two-phase flow is the sum of the gravitational, frictional and momentum pressure drop.
  gravitational pressure drop:
  frictional pressure drop:
  momentum pressure drop:
The void fraction is the ratio of the area of the pipe cross-section that is occupied by the vapor phase to the total cross-section.
(p,T), (p,T), S)
slip ratio:
+
Source: H. Kirsch, Cooling Circuit Design for the Large-scale Liquid Argon Detectors in the ICARUS Experiment, CERN-THESIS-2016-438

## Slide 32
Experimental Set-up
TT
LN2 Dewar
4 bar
Precooler
EH 1
EH 2
EH 3
Joule-Thomson expansion
Sample
FT
PT
1
2
3
4
5
6
PT
TT
Cryostat with thermal shield
Test conditions | 
Pressure (bar abs.) | 2.8
Internal diameter (mm) | 6.0
Mass flow (g/s) | 1.44
Mass velocity (kg/m2s) | 51
p
h
1
2
3
4
5
6
EH 1
EH 2
Test
LN2
1 bar

## Slide 33: Appendix
Two-phase flow CO2 in mini-channels

## Slide 34: CO2 two-phase flow in mini channels
Pressure drop and heat transfer study in a horizontal mini-channel as a function of:
  vapor quality
  mass flux
  heat flux
  psat and Tsat

## Slide 35
CO2 two-phase flow - Pressure drop

## Slide 36
CO2 two-phase flow - Pressure drop
From: D. Helmer, Investigation of Heat Transfer and Pressure Drop Phenomena of CO2 in Two Phase Flow
100
10
Pressure drop and or heating two-phase flow is cooling!

## Slide 37
CO2 two-phase flow - Heat transfer (heat and mass flux dep.)
d=1.4 mm
Mass flux dep. at low heat flux
Mass flux dep. at high heat flux

## Slide 38
CO2 two-phase flow - Heat transfer (temperature dependency)
d=1.4 mm
Temperature dep. at low heat flux
Temperature dep. at high heat flux