## Slide 1: FOM Week 28 Summary of the Reports from the Accelerators and Facilities 08 June 9AM  15 June 9AM
P.K. Skowronski (FOM)
C. Pruneaux (TI)
J.-B. Lallement (LINAC4)
F. Roncarolo (PSB)
L. Fadakis (ISOLDE)
Y. Dutheil (PS)
L. Nevay (EA, NA)
M. Bacak (nTOF)
L. Ponce (AD)
P. Arrutia (SPS)
M. Bergamaschi (AWAKE)
R. Scrivens (LINAC3)
P. Korysko (CLEAR)
D. Nisbet (LHC)

## Slide 2: Summary of TI report
Coordination: Clement Pruneaux  Ronan Ledru
Issues
  Mon 10:27: Trip of the NA62 Giga Tracker cooling system due to a false signal sent from the DSS (Detector Safety System)
    A circuit breaker has been exchanged by EN-EL in BAA85.
    DSS issue solved the 09/07
  Tue 16:41: RD5 Cryo Coldbox trip in North Area.
    At the same time was an intervention of EN-CV on the raw water, but this don’t seem to be linked.
    Investigation by EN-CV ongoing
  Tue 21:01 and 21:04: Glitch, fault of 400kV line between Grosne and Saint Vulbas
  Fri: Electrical glitch, fault of 400kV line between Albertville and Montagny Les Lanches 1
  Fri: High level alarm on the sump in UD68
    After the LHC dump, EN-CV onsite to manually empty the sump.
    High level sensor exchanged and pump1 locked off
  Sun: During a piquet intervention of the Fire detection system, the fire doors in SPS in sextant 2-3 were closed.
Alarms | 4723
ODMs | 124

## Slide 3: Summary of LINAC4
Quiet week with 3 faults leading to 3 beam interruptions of about 40 minutes each.
  Total downtime: 2 hours.
Issues
  Tuesday, a a module of the chopper supply had to be replaced by the expert [45 min].
  Tuesday, the dipole magnet LT.BHZ20 tripped because of a water flow interlock. Restarted after the Piquet intervention [40 min].
  Thursday, another trip of a dipole because of a water flow interlock but in LT.BHZ30.
    During his intervention, the Piquet increased the water flow and check the 3 dipoles (BHZ20, BHZ30 and BHZ40).
Intervention request:
  Follow-up on the L4L.RLF.121 issue last week: EPC would like to replace the power crates of the L4L solenoids at the next available occasion, although not urgently.
  Estimated duration: 2h.
  Preferred time: not critical, can wait for a good occasion
    A list of experts was provided. Nevertheless, in case of issues with one of the Linac4 solenoids, the EPC piquet could replace the crate.
LINAC4 | 98.8 % | Coordination: Jean-Baptiste Lallement  Giula Bellodi

## Slide 4: Summary of PSB
Activities
  LHC_BCMS25_LowTail_2024.regularly checked in the PSB and provided for LHC filling
  Fulfilled as much as possible (w.r.t. to other users/requests in the supercycle) the HRS requests for changing target intensities and have special extraction patterns (e.g. N consecutive extractions separated by N+1 PSB cycles not extracted to HRS)
  Following last week report on PSB to PS energy matching
    Applied to all PSB operational users
    MD users will be re-matched ‘on demand’ before MD to avoid lengthy work for all existing MD cycles variants
  Tested triple harmonic at injection for BCMS like beams
  Fri morning, profiting of SPS stop, access to check BR.QDE11 water leak (19 days after previous access)
    leak rate ~doubled w.r.t. last measurement, still acceptable for operation
    Spare magnet should be in bldg. 361 during next days
    Did not manage to fix second camera (can’t move position, BE-CEM following up). Another access needed.
PSB | ISOLDE: 96.5 % | PS: 96.5 % | Coord.: Federico Roncarolo  Chiara Bracco

## Slide 5: Summary of PSB
Issues
  Fri: access (agreed in shadow of SPS downtime) for BR.QDE11 inspection [1h25min]
  Fri: BPM FEC not responding, preventing OP to set > 0 turns [55min]
    BI expert performed power cycle FEC
    OP will change the control chain such that this kind of faults do not affect the beam production
  Sat: BI3.KSW trip: ABT piquet changed power supply [2h26min]
Intervention request
  Replace camera (for BR.QDE11 water leak remote inspection)
  Duration of 1h
  Preferred time: not critical, can wait for a good occasion
PSB | ISOLDE: 96.5 % | PS: 96.5 % | Coord.: Federico Roncarolo  Chiara Bracco

## Slide 6: Summary of ISOLDE
Activities
  HRS – REX-HIE ISOLDE Experiment IS686 on ISS with 108Sn (Tin)
    We would like to thank our PSB colleagues for facilitating our users request to stack proton pulses together and keep them in same numbers-
    Preparation on the LINAC started on Monday, by Tuesday a reference set up with A/q=3.333 (20Ne6+).
    Tuesday was the start of the preparation on the low energy side of ISOLDE.
    Set up of stable beam on 118Sn. RILIS Optimisation
      To facilitate beam tuning, switching to 87Rb for a more stable beam, was necessary.
      Energy matching between low energy part of ISOLDE and the normal conducting LINAC (REX)
    Thursday, delivered stable beam to users set up for beam tuning optimization, into their chamber.
    Delivered radioactive 108Sn32+ on Friday afternoon.
  GPS: Repair of HT Faraday Cage door was successful
ISOLDE | GPS n.a. | HRS 97.0 % | HIE 97.5% | Supervision: Leftéris Fadakis  Erwin Siesling

## Slide 7: Summary of ISOLDE
Issues
  Small Vacuum leak in CA0, a leak test will be scheduled in the following days to identify the exact spot and/or instrument that it is causing this.
  Fri: HRS Power supply of Separator Magnet 90 went into internal reference and beam was lost.
    Returned to normal after a power cycle in situ.
  HRS HT Power supply trip, OK after a reset
  Sat: users noticed a significant decrease of 108Sn
  RILIS: First step laser drifted away from nominal position causing a beam loss.
    On site intervention was required.
  REX-ISOLDE: Much work required to recover transmission losses on the REX part of the LINAC
  HIE-ISOLDE: SRF cavities were tripping so the gradient had to be redistributed amongst the last 3 SRF to decrease the power.
Plans
  Perform beam energy measurement on 108Sn32+
  Scale the whole machine to 110Sn32+ and perform another beam energy measument
ISOLDE | GPS n.a. | HRS 97.0 % | HIE 97.5% | Supervision: Leftéris Fadakis  Erwin Siesling

## Slide 8: Summary of PS
Activities:
  Bunch length scanning for AD MD to optimise antiproton yield
  TOF beam setup remains at 28ns for now, pending the need to accommodate longer bunch length for big EAST parasitic TOF beam
  BLM monitoring restored for all cycles in PS ring and TT2
  PSB->PS energy matching for all beams
Issues:
  LHC beam splitting issues on Saturday when 2 bunches had higher intensities
    Solved with manual adjustment after the LHC fill
  Affected by electrical glitch on Friday evening
  Power converter water cooling fault in F16 and adjustment on Sunday
PS | EAST N | 95.4 % | EAST T8 | 95.4 % | EAST T9 | 95.4 % | Coordination: Yann Dutheil  Bettina Mikulec
 | AD | 95.8 % | nTOF | 95.8 % | SPS | 95.8 % | 

## Slide 9: Summary of EAST Area
Activities
  T09: Good operation.
  T10: Good operation.
No issues
Plans
  T09: MPGDCAL continues.
  T10: IDEA CC continues.
  T11: No user.
EAST | T8 94.8% | T9 94.8 % | Coordination: Laurence Nevay  Bastien Rae
 | T10 94.8% | T11 N.A. | 

## Slide 10: Summary of nTOF
Coordination: Michael Bacak  Michael Bacak
Activities
  Smooth data taking in all experimental areas
  Mounting of the Ar(n, g) experimental set-up in EAR2 and start with the container gaseous target still empty
No issues
Plans: many interventions are in program during the Technical stop
  EAR1: ending of Er(n, g) and starting of Cu(n, g) measurements
  EAR2: Ar(n, g), measurements at different gas pressure (200-300 bar)
  NEAR: activation measurements
Access request: July 17 from 8h to 16h

## Slide 11: Summary of AD
Summary
  Good week in terms of availability but several periods of degraded performance alternating with good ones
Activities
  Reduced intensity over the week-end due to degraded mode of the AD magnetic horn
    Reduced pulse voltage resulting in ~10 % loss in pbars yield
  Access in AD for He refill of the BCCCA
  MD on varying proton bunch length and emittance with a single bunch to observe pbars yield dependence on these parameters
AD | 88.0 % | Coordination: Laurette Ponce  Laurette Ponce

## Slide 12: Summary of AD
Issues
  Communication problem with several Pow1553 power converters in FTA, DI, DE line and e-cooler solenoid:
    Very tricky diagnostics of a very old system in the absence of the specialist
    Joint effort of BE-CEM (pow1553 controls) and first line (HW) to find a loose cable on a spare power converters in the loop.
  2 possible flash-overs in AD magnetic horn
    reduced pulse voltage by 2 times 500 V and resume operation in degraded mode over the week-end
  ELENA transfer line ISEG power converters in communication error AGAIN!
  ELENA tune meter power cable found unplugged
Plans
  Diagnose problem with the horn and try to recover nominal operation
AD | 88.0 % | Coordination: Laurette Ponce  Laurette Ponce

## Slide 13: Summary of SPS
Marked by the downtime on Thursday-Friday due to a vacuum leak in 200MHz cavity 3.
  The intervention to fix the leak was performed very efficiently by all the teams involved.
  The rest of the week went smoothly, producing beams for LHC, North Area, AWAKE and parallel MDs. There was no dedicated MD this week.
LHC:
  Continued filling with low-tails beam.
  Misbehaviour of bend on TI2 caused injection oscillations (~2.5 mm), which led to mini-quench in LHC due to showers from injection. collimator -> FEI limits being assessed.
  Filling interrupted due to faulty PS bend.
NA:
  No major issues. Few difficulties with spill quality due to super-cycle composition and after beam stops.
AWAKE:
  Provided single bunch at an intensity of 3e11.
  Improved LSS4 orbit flatness at extraction -> reduced losses by 50%
SPS | LHC: 83.4% | NA: 77.0% | AW: 95.1% | Coord.: Pablo Arrutia  Carlo Zannini

## Slide 14: Summary of SPS
Issues
  Vacuum leak on cavity 3 [~23h]:
    The SPS cavity 3 (Thales power plant, 200MHz) triggered a vacuum interlock on Thursday ~13h.
    A leak detection test identified that the leak was coming from a Higher Order Mode (HOM) coupler.
    The HOM coupler was burnt and was swiftly replaced by a spare.
    Some other HOM couplers were inspected and found to be OK.
    The cavity had to be re-pumped and re-conditioned.
    A final leak test identified no additional issues, fully recovering from the fault on Friday ~12h.
  Main power converters down [~3h]:
    Just after the RF had recovered and hopes were up for the beam to be back, the main PCs went into fault.
    The issue was fixed by replacing Watchdog Interlock Controller (WIC) card in BA3.
  Mis-driven settings when mapping new cycle [~1.5h]:
    LSA-to-HW drive did not execute correctly for FEI in TT10.
    Not easy to find error in SIS -> Assessing best way to display this problem to identify it quicky in the future.
  Misbehaviour of power converter in TI2 bend:
    The current was within FEI limits, but injection oscillations (~2.5mm) still caused enough collimator showers to produce mini-quench at LHC -> being followed up.
SPS | LHC: 83.4% | NA: 77.0% | AW: 95.1% | Coord.: Pablo Arrutia  Carlo Zannini

## Slide 15: Summary of SPS
Plans
  T4 target intensity change on Wednesday
  Dedicated MD on Wednesday:
    Access possible in NA only until 2pm (TT20 TED in)
    After 2pm TED out: beam to P42
SPS | LHC: 83.4% | NA: 77.0% | AW: 95.1% | Coord.: Pablo Arrutia  Carlo Zannini

## Slide 16: Summary of NORTH Area
Coordination: Laurence Nevay  Bastien Rae
Issues
  H2: Moving beam issue observed again, related to change of beam files in H8.
  H4: Problem in HP XCET has been identified by the BE-EA and SY-BI teams, tests pending the return of the SPS beam.
  H6: One brief fault in Bend 1 power supply.
Plans
  Change to T4 standard wobbling and 100 mm target head on Wed. 17.07, then also back to the standard 42 units on T4. Need 150 units on T6 on the morning of 19.07 for M2 high-intensity RP test.
  H2: ΝΑ61 continues.
  H4: NP04 continues.
  H6: MuonE ECAL → DRD6 MAXICC.
  H8: Atlas TRT → Atlas TRD (change of main user, both stay).
  M2: AMBER continues. High intensity RP test planned for the morning of Friday, 10.07.
  K12: NA62 will go back to standard data taking on Wednesday, 17.07
Availability |  |  |  |  | 
H2 | 75.2 % | H6 | 75.1 % | K12 | 75.2 %
H4 | 75.2 % | H8 | 75.2 % | M2 | 75.2 %
Target sharing |  |  |  |  |  |  | 
T2 | 30 | T4 | 20 | T10 | 1 | T6 | 30

## Slide 17: Summary of AWAKE
Coordination: Michele Bergamaschi  Michele Bergamaschi
Issues
  Tuesday: Failure of one of plasma source heaters replaced on Thursday access
  Wednesday: Access system problem preventing to go to beam mode (door YDPC02.TCV4 hardware veto) required intervention from access system technicians
  Friday: Cavity repair and mains of SPS down
  Sunday: Power supply of plasma source chillers and new control rack, found a PSU 48V in the rack faulty, replaced with a spare
 | M | T | W | Th | F | S | S
SPS extractions to AWAKE | 140 | 234 | e-beam | MD | 34 | 1155 | 396
Hours of beam to AWAKE | 1.3 | 2.2 | e-beam | MD | 0.4 | 6.9 | 2.6

## Slide 18: Summary of LINAC3
Coordination: Detlef Kuchler
Activities
  Monday to Wednesday tests of a software agent for the source. The aim is to develop a tool to support the tuning and stability of the source.
  Thursday the Sairem2 microwave generator was checked by a representative of the company. The issue was tracked down to the HV supply. This will be shipped now for repair to the company. A spare power supply should be delivered soon (ordered already last year).
Issues
  The source performance is still limited due to discharges. By the end of this week we have to see if it could condition away or if we have to open to source to replace the entire extraction system

## Slide 19: Summary of CLEAR
Coordination: Pierre Korysko  To be defined
Activities
  Last week was dedicated to medical applications: Irradiations of Zebra Fish Eggs (ZFE) with Very High Energy Electron (VHEE) at Ultra High Dose Rate (UHDR) and Conventional Dose Rate (CDR) for cancer treatment and FLASH effect studies with Hôpitaux Universitaires de Genève (HUG).
No major issues
Plans
  This week is dedicated to the same experiment (ZFE irradiation for FLASH effect Studies) with Hôpitaux Universitaires de Genève (HUG).

## Slide 20: Summary of LHC
Started the week with access to exchange the emulsions for FASER and SND. This was followed by 24hrs of good luminosity production.
This was followed by a rocky 48hrs with several fills dumped due to faults. This included a large quench following a UFO in S45 causing 12hr downtime.
Production was also suspended while the SPS repaired and recovered from a vacuum leak in their RF system.
There were a series of faults on Friday night, including a failed pump for a water sump in the UD68 dump area which caused a L3 alarm to the fire brigade and subsequent intervention to prevent flooding.
Finally at the weekend we could resume normal operation, with Saturday and Sunday producing good availability and luminosity production.
Availability: 63% Stable beam ratio: 45%
Machine coord.: David Nisbet  Mirko Pojer

## Slide 21: Summary of LHC
Issues
  PC interlock dumped beams due to loss of communication with FEC cfc-sr2-rl2a
  Poor quality Q signal caused Qfb to dump at EoR
  Beam induced quench in S12 following a bad injection from TI2 due to a power converter issue – FEI tolerances to be reviewed.
  UFO induced quench in S45, and UFO dump in 25R3
  BCCM triggered correctly when RF tripped due to a power converter fault
  Faulty RF tuner electronics on line 4B2 dumped beam (access made to repair)
  Tempestive fault of RB.A56 power converter
  Flooding in UD68 raised a Level3 alarm to the fire brigade. Significantly degraded material in this area needs maintenance and consolidation.
  Experiments:
    ALICE solenoid water leak (now repaired, but power cycling of magnet to be minimised)
    LHCb VELO lost position due to damaged track (repaired and validated with beam)
Availability: 63% Stable beam ratio: 45%
Machine coord.: David Nisbet  Mirko Pojer