## Slide 2: BDF Project: Cooling and Ventilation Infrastructure and Target CV Systems
CV Technical Review
Pietro Avigni, Michele Battistin

## Slide 3: Outline
BDF Project
  Overview of the Project
  Cooling Design
  Ventilation Design
BDF Target Prototype (TCC2)
  Target and Target Prototype Design
  Cooling Skid Design
  Installation and Testing
BDF Helium Passivation System
  Overview and Process Description
  Selection of Components
  Budget & Schedule

## Slide 4: Outline
BDF Project
  Overview of the Project
  Cooling Design
  Ventilation Design
BDF Target Prototype (TCC2)
  Target and Target Prototype Design
  Cooling Skid Design
  Installation and Testing
BDF Helium Passivation System
  Overview and Process Description
  Selection of Components
  Budget & Schedule

## Slide 5: BDF Introduction
BDF is a planned high intensity fixed target facility in the North Area of the SPS for beam dump experiments
High intensity proton beam:
  Pulsed power deposition: 2.5 MW over 1 second, repeated every 7.2 seconds (Cyclic);
  355 kW average beam power over time;
Dense target/dump to maximize particle interaction/production;
Facility designed so that can be reused for multiple experiments;
First experiment to be hosted: SHiP (Search for Hidden Particles);
Minimal impact on running the North Area program.

## Slide 6: BDF Layout
Target Complex
Experimental Area
Google Maps
Jura
Salève
Beam direction
Extraction Tunnel
TDC2
Auxiliary Building
Access Building
Junction Cavern
Full integration from transfer line to experimental area completed
Locations of structures and services defined and optimized in terms of radiation protection, safety and accessibility.
TCC2
BA80

## Slide 7: BDF Naming

## Slide 8: BDF Video: Facility Overview

## Slide 9: BDF Video: Target Complex

## Slide 10: BDF Extraction Area
Google Maps
Beam direction
Extraction Area

## Slide 11: BDF Extraction Area
Junction Cavern
Extraction Tunnel
Auxiliary Building
Access Building
30t crane
Shaft
Lorry
access
False floor
Crane
Access control
TT90
TDC2
BDF beamline
BDF beamline
Transport accessway
Ventilation

## Slide 12: BDF Target Complex
Target Complex
Google Maps
Beam direction

## Slide 13: Two technical solutions
Target is located 15 m underground, relatively close to the CERN fence (~70 m)
Cast-iron and steel shielding enclose target (3700 tonnes)
Target bunker inside an active circulation He-vessel
Fully remote handling/manipulation during the lifetime of the facility
Target complex design developed in detail  demonstrated feasibility of construction, operation, maintenance and decommissioning
Crane handling solution
Shielding, supports, target, moved by crane
Trolley handling solution
Target and services on trolleys on rails
SPS beam

## Slide 14: BDF Experimental Area [SHiP]
Experimental Area
Google Maps
Beam direction

## Slide 15: BDF Experimental Area [SHiP]
Experimental Hall
Surface Hall
Service Building
Decay volume
Muon shield
SHiP magnet
3 access points
20 m
80 m

## Slide 16: BDF Provisional Schedule
We are here
(Q1 2019)
Project approval
(Possible date)

## Slide 17: BDF CV Design
 | Cooling Systems | Ventilation Systems | Other Systems
Extraction Area | Magnets Power converters Primary system Cooling towers (Chilled water) | Tunnel Auxiliary building Access building Evaporators room (TBC) | Compressed air Rising system
Target Complex | Target Proximity shielding Magnetic coil Helium circulation Helium Passivation | Surface hall Access Area Hot Area | Compressed air for draining Rising system Evaporation system Smoke extraction
Experimental Area | Magnets Power converters | Surface Hall Experimental Hall Service Building | Compressed air Rising system Smoke extraction
Let’s see the cooling and the ventilation design now…

## Slide 18: BDF Cooling Requirements
Equipment | Number of equipment | Tin | Delta T | Tout | Flow / unit |  | Dissipated power / unit | Total dissipated Power | Pin | Pressure drop | Pout | Total flow | Type of water | Activated water?
 |  | (°C) | (°C) | (°C) | (l/min) | (m3/h) | (kW) | (kW) | (bar) | (bar) | (bar) | (m3/h) |  | 
QTG.01 | 1 | 27 | 7.3 | 34.3 | 6.9 | 0.4 | 3.5 | 3.5 | 7.5 | 6 | 1.5 | 0.4 | Demineralized | Yes
QTL.02 | 1 | 27 | 7.5 | 34.5 | 26.0 | 1.6 | 13.6 | 14 | 7.5 | 6 | 1.5 | 1.6 | Demineralized | Yes
QTL.03 | 1 | 27 | 5.8 | 32.8 | 26.0 | 1.6 | 10.6 | 11 | 7.5 | 6 | 1.5 | 1.6 | Demineralized | Yes
QTL.04 | 1 | 27 | 2.3 | 29.3 | 26.0 | 1.6 | 4.2 | 4.2 | 7.5 | 6 | 1.5 | 1.6 | Demineralized | Yes
QTL.05 | 1 | 27 | 7.9 | 34.9 | 26.0 | 1.6 | 14.4 | 14 | 7.5 | 6 | 1.5 | 1.6 | Demineralized | Yes
QTL.06 | 1 | 27 | 12.5 | 39.5 | 26.0 | 1.6 | 22.6 | 23 | 7.5 | 6 | 1.5 | 1.6 | Demineralized | Yes
MBB | 5 | 27 | 15.2 | 42.2 | 57.1 | 3.4 | 60.7 | 303 | 13.5 | 12 | 1.5 | 17.1 | Demineralized | Yes
MBN | 18 | 27 | 15.4 | 42.4 | 27.7 | 1.7 | 29.8 | 536 | 2.5 | 1 | 1.5 | 29.9 | Demineralized | Yes
MDXl | 6 | 27 | 3.7 | 30.7 | 7.3 | 0.4 | 1.9 | 12 | 7.5 | 6 | 1.5 | 2.6 | Demineralized | Yes
MDXl dill | 6 | 27 | 3.3 | 30.3 | 7.3 | 0.4 | 1.7 | 10 | 7.5 | 6 | 1.5 | 2.6 | Demineralized | Yes
Water-cooled cables | 1 | 27 | 17.2 | 44.2 | 167 | 10.0 | 200 | 200 | 6.5 | 5 | 1.5 | 10.0 | Demineralized | Yes
Power converters | 1 | 27 | 3.3 | 30.3 | 660 | 39.6 | 150 | 150 | 4.5 | 3 | 1.5 | 39.6 | Demineralized | No
Equipment | Number of equipment | Tin | Delta T | Tout | Flow / unit |  | Dissipated power / unit | Total dissipated Power | Pin | Pressure drop | Pout | Total flow | Type of water | Activated water?
 |  | (°C) | (°C) | (°C) | (l/min) | (m3/h) | (kW) | (kW) | (bar) | (bar) | (bar) | (m3/h) |  | 
Emulsion spectrometer magnet | 1 | 27 | 15.1 | 42.1 | 1800 | 108 | 1900 | 1900 | 13 | 12 | 1 | 108 | Demi | No
Decay volume / vacuum | 1 | 27 | 40.9 | 67.9 | 6.67 | 0.40 | 19 | 19 | 13 | 12 | 1 | 0.40 | Demi | No
Main spectrometer magnet | 1 | 27 | 14.3 | 41.3 | 1084 | 65.0 | 1083 | 1083 | 13 | 12 | 1 | 65.04 | Demi | No
Power converters | 1 | 27 | 3.8 | 30.8 | 480 | 28.8 | 126 | 126 | 4.5 | 3 | 1.5 | 28.8 | Demi | No
Equipment | Number of equipment | Tin | Delta T | Tout | Flow / unit |  | Dissipated power / unit | Total dissipated Power | Pin | Pressure drop | Pout | Total flow | Type of water | Activated water?
 |  | (°C) | (°C) | (°C) | (l/min) | (m3/h) | (kW) | (kW) | (bar) | (bar) | (bar) | (m3/h) |  | 
Target | 1 | 27 | 6.7 | 33.7 | 750 | 45 | 350 | 350 | 22 | 3.5 | 18.5 | 45 | Demineralized | Yes
Proximity shielding | 1 | 27 | 3.0 | 30.0 | 96 | 5.76 | 20 | 20 | 2 | 1 | 1 | 5.76 | Demineralized | Yes
Magnetic coil | 1 | 27 | 8.6 | 35.6 | 250 | 15 | 150 | 150 | 20 | 19 | 1 | 15 | Demineralized | Yes (Not much)
Extraction Area (WP: EDMS 2050765)
Target Complex (WP: EDMS 2050757)
Experimental Area (WP: EDMS 2050772)

## Slide 19: BDF Cooling Design
Extraction Area
Experimental Area
Target Complex
Type of cooling | Extraction Area [kW] | TC [kW] | Exp. Area [kW] | BDF complex TOTAL [kW]
Demineralized water | 1300 | 600 | 2200 | 4500
Chilled water | 185 | 135 | 450 | 770

## Slide 20: BDF Cooling Synoptic (CS)
Extraction Area
Target
Complex
Experimental
Area

## Slide 21: Extraction Area CS

## Slide 22: Target Complex CS

## Slide 23: Experimental Area CS

## Slide 24: BDF Primary Cooling
Extraction Area
Experimental Area
Target Complex

## Slide 25: BDF Primary Cooling
4500 kW nominal, 600 m3/h
3 CT (N+1 redundancy) 2500 kW each
DT: 7 K (9 K for high power SHiP magnet)
2 pumps (N+1) in auxiliary building
Option 1 Local cooling towers | Option 2 CT2 cooling towers
Operation independent from other cooling systems in the Prevessin area | Operation dependent on CT2 towers availability
Operation and maintenance more complex (water treatment, etc.) | No added complexity from operation and maintenance standpoint
Potential activation confined to new experimental area | Potential activation spreading over CT2 cooling system
Requires installation of cooling towers and pumping station on the new site | Requires the upgrade of the CT2 pumps and a new pipeline (technical gallery)

## Slide 26: Helium Vessel CV Systems

## Slide 27: Target Water Cooling System
Extraction Area
Experimental Area
Target Complex

## Slide 28: Target Water Cooling System
On trolley
Secondary demi water,
350 kW on average
Double-wall heat exchanger: prevent cross-contamination
EPDM OK for gaskets
Automated filling, pressurization and draining
Radioactive area: pneumatic actuators

## Slide 29: BDF Shielding & Magnet Cooling
Extraction Area
Experimental Area
Target Complex

## Slide 30: BDF Shielding & Magnet Cooling
2 circuits:
  Shielding: 20 kW
  Magnet: 150 kW
Demineralized water
Redundant shielded cartridges
Investigating He cooling for magnet
CV room
CV room: lowest level

## Slide 31: BDF Target Helium Circulation
Extraction Area
Experimental Area
Target Complex

## Slide 32: BDF Target Helium Circulation
Parameter | Unit | Value
Location | - | Trolley
Flow rate | g/s | 4.1
Changes per hour | 1/h | 1000
T in | °C | 28
T out max | °C | 50
DT max | °C | 22
Thermal load | kW | 0.5
Piping size | - | DN25
Pressure supply | bara | 1.1
Pressure drop | Pa | 6000
Purpose:
Blow helium around target containment;
Detect leaks from target containment;

## Slide 33: BDF Helium Passivation
Extraction Area
Experimental Area
Target Complex

## Slide 34: BDF Magnets Cooling
Extraction Area
Experimental Area
Target Complex

## Slide 35: BDF Magnets Cooling
Extraction Tunnel
Experimental Area
1200 kW, 75 m3/h, 41°C
20 bar, demi water
Cooling station in auxiliary building
2200 kW, 185 m3/h, 37°C
Demi water
Cooling station in service building

## Slide 36: Chilled Water and Rising System
Technical Gallery, options:
Evaporation System

## Slide 37: BDF Ventilation Requirements
Ventilation Area | T Range [°C] | RH range [%] | Min Heat Load [kW] | Max Heat Load [kW] | RP Class
Extraction tunnel | 18-26 | <70% | -33 | 28 | NC
Access building | 18-26 | - | -22 | 8 | NC
Auxiliary building | 18-26 | <70% | -102 | 138 | NC
Ventilation Area | T Range [°C] | RH range [%] | Min Heat Load [kW] | Max Heat Load [kW] | RP Class
Surface hall | 18-26 | - | -129 | 48 | C1
Access area | 18-26 | <70% | -3 | 6 | C1
Hot area | 18-24 | <70% | -2 | 16 | C2
Ventilation Area | T Range [°C] | RH range [%] | Min Heat Load [kW] | Max Heat Load [kW] | RP Class
Experimental hall | 18-26 | 40-70 | -75 | 253 | NC
Surface hall | 18-26 | - | -173 | 57 | NC
Service building | 18-26 | <70 | -49 | 125 | NC
Extraction Area (WP: EDMS 2050765)
Target Complex (WP: EDMS 2050757)
Experimental Area (WP: EDMS 2050772)

## Slide 38: BDF Dynamic Confinement Requirements
RP requirements: ISO 17873:2004(E)
Row Labels | Tot Volume [m3] | Min RP flow [m3/h]
C1A | 28 786 | 28 800
C1B | 618 | 1 250
C1C | 291 | 1 200
C2A | 901 | 1 800
C2B | 746 | 3 750

## Slide 39: BDF Ventilation Synoptic (VS)
Extraction
Area
Target
Complex
Experimental
Area

## Slide 40: BDF VS Extraction Area

## Slide 41: BDF VS Target Complex

## Slide 42: BDF VS Experimental Area

## Slide 43: Extraction Area Ventilation
AHUs in auxiliary building
Activation only for Tunnel
No dynamic confinement
Extraction only during shutdown

## Slide 44: TC Ventilation
AHUs in auxiliary building
Pressure cascade from -20 Pa to -100 Pa
3 classes: C1A, C1B, C2
Extractors for depressurization

## Slide 45: TC Hot Area HVAC Flownex
Humidity source
Air leakage
Heat loads
Regulation approach (PID controller, control components)
Sizing (piping, dampers, control valves)

## Slide 46: Experimental Area Ventilation
AHUs in service building
No activation expected
No dynamic confinement
CFD for underground flow

## Slide 47: Outline
BDF Project
  Overview of the Project
  Cooling Design
  Ventilation Design
BDF Target Prototype (TCC2)
  Target and Target Prototype Design
  Cooling Skid Design
  Installation and Testing
BDF Helium Passivation System
  Overview and Process Description
  Selection of Components
  Budget & Schedule

## Slide 48: BDF Target Design
Need to dissipate around 320 kW of heating power (~5 MW/m3)
Optimized segmentation, forced water cooling
CFD simulation mainly by CV
Thermo-mechanical design
~1.5 m
Ø250 mm
  1st part: TZM core
  Molybdenum alloy, higher strength and recrystallization temperature than pure Mo
  2nd part: Tungsten core
  High-Z and good performance under irradiation
  Ta/Ta2.5W cladding

## Slide 49: BDF Target Proto
Reliability of the target is a critical aspect for the design of BDF
  Representative beam test executed before LS2
Reduced scale prototype
  Reduced diameter (80 mm)
Experimental setup installed in TCC2, upstream T6 primary target
High intensity beam on target during >14 h (45 kW deposited ~6 MW/m3)
  Online measurements performed
  Good correlation with simulations
Validation of final target operational conditions

## Slide 50: BDF Target Prototype

## Slide 51: P&ID prototype target cooling skid
Installed in TA801 to supply cooling in TCC2

## Slide 52: Installation – BA80
TCC2
TA801
TA801
TA801
TCC2

## Slide 53: Skid in TA801
Start date | End date | Monitoring System | R-factor | ΦHEH [pp/cm2] | ΦThN [pp/cm2]
19/09/2018 | 17/10/2018 | BatMon pair | 7.8* | 5.11 x 108 | 4.00 x 109
 |  | RadMon 1 | 45.4 | 6.26 x 106 | 2.84 x 108
 |  | RadMon 2 | 29.0 | 2.31 x 107 | 6.69 x 108

## Slide 54: R2E - LOFC

## Slide 55: Outline
BDF Project
  Overview of the Project
  Cooling Design
  Ventilation Design
BDF Target Prototype (TCC2)
  Target and Target Prototype Design
  Cooling Skid Design
  Installation and Testing
BDF Helium Passivation System
  Overview and Process Description
  Selection of Components
  Budget & Schedule