## Slide 1
Technical InfrastructurE AVailability
Challenges and opportunities from LHC to FCC-ee
Hannah Dostmann, Jack Heron,
Lukas Felsberger, Daniel Wollmann, Jan Uythoeven

## Slide 2
Stable Beams
Operation
Down Time
FCC-ee:
365 days
−120 (extended shutdowns)
− 30 (annual commissioning)
− 20 (machine development)
− 10 (technical stops)
185 days for physics
min 75% !
Availability and Efficiency
20 May 2025

## Slide 3: Simulation Environment
FCC-ee
MTBF
Mean
Down Time
Stable Beams
Operation
Default
Repair completed
Main ring failure
Injector Complex failure
 | Z | W | H | tt
Fill time (min) | 7.7 | 2.5 | 1.52 | 1.45
Lifetime (min) | 15 | 12 | 12 | 11
Polarisation (min) | 90 | 90 | 0 | 0
 | Z | W | H | tt
 | 7.7 | 2.5 | 1.52 | 1.45
 | 15 | 12 | 12 | 11
 | 90 | 90 | 0 | 0
Availability
Luminosity
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025
3

## Slide 4
FCC-ee Forecast
Electrical Network
Cryogenics
Cooling and Ventilation
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025
More details:
  “Availability, Efficiency and Integrated Luminosity”
  Jack Heron, 23th May, Machine Protection and Availability

## Slide 5: Cooling & Ventilation
Acknowledgment: Guillermo Peon, Inigo Martin Melero, Andrew Nicholas Coleman
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025

## Slide 6: Cooling & Ventilation
MTBF scaled by number of critical circuits
Same repair duration as the LHC
FCC-ee
With child systems
CV only
MTBF
Mean Down Time
LHC
Proton and Ion runs from start of stable beams to end of physics, excluding machine developments and technical stops (2015-2024)
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025
Down Time [h]

## Slide 7: Cryogenics
Acknowledgment: Laurent Delprat
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025

## Slide 8
Cryogenics – LHC
Beam screen regulation related issues
Helium level oscillations (distribution feed box)
Helium level oscillations (standalone magnets)
With child systems
Cryogenics only
Proton and Ion runs from start of stable beams to end of physics, excluding machine developments and technical stops (2015-2024)
Specific to superconducting magnets
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025

## Slide 9: Cryogenics – FCC-ee
Cryoplants for RF system located at PH & PL
MTBF scaled according to power level eq @ 4.5K
not modeled yet!
PL (Booster)
    Z,W & ZH Machine : 1 x 13.3 kW eq @ 4.5K
    tt Machine: 2 x 22 kW eq @ 4.5K
https://cds.cern.ch/record/2928793/files/2505.00274.pdf
PH (Collider)
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025
~40 kWeq @ 4.5K
82 kWeq @ 4.5K

## Slide 10: Cryogenics – FCC-ee
R&D Opportunities
FCC-ee will use Turbo Brayton Cycles which are supposed to be more reliable
  positive effect on all “Production” faults
2 plants at one location will provide some redundancy
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025

## Slide 11: Electrical Network
Acknowledgement: Mario Parodi, Charline Marcel
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025

## Slide 12: Electrical Network
External Network Perturbations
https://cds.cern.ch/record/2888389/files/Map%20V0500.jpg?subformat=icon-1440
FCC
Power in FCC-ee comes from two transmission lines with node at Genissat
External perturbations should appear at twice the rate of LHC (conservative assumption)
Genissiat
Line 1
Line 2
PA
PD
PH
LHC
LHC
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025
With child systems
External Perturbations only
Proton and Ion runs from start of stable beams to end of physics, excluding machine developments and technical stops (2015-2024)

## Slide 13: Electrical Network – FCC-ee
*https://indico.cern.ch/event/1509818/contributions/6353584/attachments/3010188/5307118/RF_powering_6_Feb_2025_Davide.pdf
4 substations
3 substations
1 substation
MTBF should scale with the number of substations at PA,PD & PH
Mean Down Time as with LHC
  Exception: redundancy in High Voltage (HV) network
   Averaged reconfiguration down time of 1h
Main RF power line at PH
From 400 kV LHC faults
Scaled by power level:
  LHC: 440 MVA
  FCC: 150 MVA (~0.34 LHC)
Internal Equipment
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025
0.34

## Slide 14: Electrical Network – FCC-ee
Most improvement to be made at High Voltage Network
The Redundancy works, but child faults must also be reduced!
Chart: Down Time FCC-ee (High Voltage)
| Parent System | Child Faults
FCC-ee | 5.4 | 94.6
Faults without children
Faults with children
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025

## Slide 15
Electrical Network - Child Faults in LHC
Chart: LHC Electrical Network Down Time 2015-2024
| Internal Equipment | Internal Child Faults | External Child Faults | External Perturbations
LHC Electrical Network Down Time 2015-2025 | 394.91 | 110.29 | 158.45 | 17.7
Child faults in other systems
40%
58%
2%
Child Fault Down Time in LHC [h]
(2015-2024 Physics Operation)
External Perturbations
Internal Equipment
Most downtime due to Cryogenics child faults
The proportions might change in FCC:
  Less cryogenics
  More RF & power converters
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025
Redundancy could be effective

## Slide 16
First - we have to better understand these perturbations
Child Systems
Detailed requirements for resilience to voltage deviations issued to relevant equipment design teams
Ensure they are given priority through the design progress
Electrical Network
“User Friendly“
Solutions to dampen voltage deviations (e.g Unified Powerflow Controllers)
Child Faults in the Technical Design Stage
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025
https://coaching-persoenlichkeitsentwicklung.ch/wp-content/uploads/2017/02/verstehen_lernen_fotolia_63574038_S-1.jpg
https://unternehmer.de/wp-content/uploads/2012/09/%C2%A9-ioannis-kounadeas-97473562.jpg

## Slide 17
Conclusion & Outlook
We have a simulation for Availability and Luminosity of the FCC-ee extrapolating from current working systems in other accelerators
Availability is one of the main challenges for integrated luminosity in the FCC
Success requires a machine-wide improvement in reliability
Cooling and Ventilation
Performance expected to be similar as in LHC
Cryogenics
Won’t be as highly ranked as it is in the LHC right now, but significant in tt
Sensitive as child to electrical network failures
R&D opportunities:
  Turbo Brayton Cycles
  Redundancy between the two cryoplants at each point
Electrical Network:
Could be one of the highest contributors to down time and luminosity losses in FCC-ee (dominated by child faults and internal equipment)
R&D opportunities:
  Reducing Child faults
  Redundancy
Both must happen in parallel !
Hannah Dostmann | Technical Infrastructure Availability - Challenges and Opportunities from LHC to FCC-ee
20 May 2025