## Slide 1
Future Circular Collider
Technical Infrastructure
Ventilation update for FCC
I. Martin Melero (EN/CV)
FCC Week 2025

## Slide 2
2
Outline
0. Definitions
1. Update on thermal toads
  1.1. Primary circuit heat loads
  1.2. Chillers
  1.3. Chilled water loads
2. Update on integration
  2.1. Technical Points: B, F
  2.2. RF Points: H, L
  2.3. Exp. Points: A, D, G, J
3. Update on tunnel concept
  3.1. General parameters
  3.2. Semi-transverse
  3.3. Longitudinal
  3.4. Adaptation Run / Access  Emergency
  3.5. Fire heat effects
  3.6. Pressure differences
  3.7. Degraded modes
4. Next steps
Inigo Martin Melero (CERN/EN/CV)

## Slide 3
3
0. Definitions
Supply air
Exhaust air
Underground
Surface
Chilled water
Supply
Return
AHUs
Fancoils
Shaft
Cavern
AHUs
Treatment of the air to temperature and humidity conditions
Supply air
Supply air
Exhaust air
Exhaust air
Recycled air
Heating battery
Cold battery
Air filter
Air filter
Air filter
Air filter
Air filter
Fancoils
Recirculation of air through coils to locally adjust temperature conditions
Chilled water
Supply
Return
Supply
Return
Chilled water
Hot air
Cold air
Heat Exchanger
Chilled water supply and return
Blower
Return AHU
Supply AHU
Inigo Martin Melero (CERN/EN/CV)

## Slide 4
4
1. Update on thermal loads
Supply air
Exhaust air
Underground
Surface
Chilled water
Supply
Return
AHUs
Fancoils
Shaft
Cavern
Chilled water
Supply
Return
TO CHILLERS
TO CHILLERS
Inigo Martin Melero (CERN/EN/CV)

## Slide 5
Inigo Martin Melero (CERN/EN/CV)
5
1. Update on thermal loads
Ventilation cooling requirements in Primary Water Circuit
Chilled water
Refrigerant
Primary water
Chiller
6°C
12°C
25°C
More info:
I. Martin Melero @ Session TIWG 5
Primary circuit heat loads
Point | Cryogenics | Experiment | General Services | Power converters RF | Chilled Water | Underground | TOTAL
A | 0.35 | 0.50 | 2.00 |  | 5.87 | 42.56 | 51
B |  |  | 2.00 |  | 5.18 | 1.05 | 8
D | 0.35 | 0.50 | 2.00 |  | 5.84 | 42.56 | 51
F |  |  | 2.00 |  | 5.18 | 1.05 | 8
G | 0.35 | 0.50 | 2.00 |  | 5.87 | 42.56 | 51
H | 34.00 |  | 2.00 | 4.50 | 11.24 | 48.95 | 100
J | 0.35 | 0.50 | 2.00 |  | 5.84 | 42.56 | 51
L | 10.00 |  | 2.00 | 0.07 | 5.71 | 2.74 | 20
Heat loads (MW) at Cooling Towers, FCC-ee ttbar

## Slide 6
6
1. Update on thermal loads
Point | Cooling power (kW) | Flow rate (m3/h) | Number of chillers | Cooling power / chiller (kW) | TOTAL (kW)
A | 4,895 | 703 | 6 | 1,000 | 6,000
B | 4,322 | 620 | 6 | 900 | 5,400
D | 4,875 | 700 | 6 | 1,000 | 6,000
F | 4,322 | 620 | 6 | 900 | 5,400
G | 4,895 | 703 | 6 | 1,000 | 6,000
H | 9,367 | 1345 | 7 | 1,800 | 12,600
J | 4,875 | 700 | 6 | 1,000 | 6,000
L | 4,757 | 683 | 6 | 1,000 | 6,000
Chillers, FCC-ee ttbar
Chilled water requirements
Chilled water
Refrigerant
Primary water
Chiller
COP ≈ 5
Increase in chillers due to cable load Tunnel
6°C
12°C
25°C
Primary water requirements
in Table p. 5
Chillers
Inigo Martin Melero (CERN/EN/CV)

## Slide 7
7
1. Update on thermal loads
Chilled water loads
2. Underground heat loads to chilled water (kW) |  |  |  |  |  | 
POINT | Cryogenics | RF | Experimental Areas | Power Converters | Ventilation UW | TOTAL
A | 10 |  | 50 | 220 | 200 | 480
B |  |  |  | 220 |  | 220
D | 10 |  | 40 | 220 | 200 | 470
F |  |  |  | 220 |  | 220
G | 10 |  | 50 | 220 | 200 | 480
H | 145 | 4,600 |  | 220 | 200 | 5,165
J | 10 |  | 40 | 220 | 200 | 470
L | 60 | 75 |  | 220 | 200 | 555
1. Surface heat loads to chilled water (kW) |  |  |  |  |  |  | 
POINT | Cryogenics | Power Converters | General Services | Experimental Areas | Shaft Pressurisation | Fresh Air for Underground Areas | TOTAL TO CHILLED WATER
A | 13 |  | 500 | 50 | 300 | 150 | 1013
B |  |  | 500 |  | 150 | 50 | 700
D | 13 |  | 500 | 40 | 300 | 150 | 1003
F |  |  | 500 |  | 150 | 50 | 700
G | 13 |  | 500 | 50 | 300 | 150 | 1013
H | 1,400* | 2,250* | 500 |  | 150 | 150 | 800
J | 13 |  | 500 | 40 | 300 | 150 | 1003
L | 402* | 35* | 500 |  | 150 | 150 | 800
*Extracted without chilled water  Option: free cooling
3. Sector heat loads to chilled water (kW) |  |  |  | 
Magnets | Cables | Synchrotron radiation absorbers | Alcoves | TOTAL PER SECTOR
352 | 2,500 | 250 | 300 | 3,402
Chilled water load
=
1. Surface + 2. Underground
+ 3. Sector
Scenario for 7 alcoves
Inigo Martin Melero (CERN/EN/CV)

## Slide 8
8
2. Update on integration
Supply air
Exhaust air
Underground
Surface
Chilled water
Supply
Return
AHUs
Fancoils
Shaft
Cavern
Chilled water
Supply
Return
TO CHILLERS
TO CHILLERS
Inigo Martin Melero (CERN/EN/CV)

## Slide 9
2. Update on integration
Inigo Martin Melero (CERN/EN/CV)
9
Technical Areas in B, F | Air Supply | Extraction | Emergency extraction
Access Mode | Ventilation Service Cavern: 40,000 m3/h | 40,000 m3/h | 40,000 m3/h
Technical Points: B, F
PF.9
PF.7
Reference | Duct Function | Size
PF.1 | Ventilation Tunnel Supply 1 | 1.2 m
PF.2 | Ventilation Tunnel Extract 1 | 1.2 m
PF.3 | Ventilation Emergency Extract 1 | 1.2 m
PF.4 | Ventilation Tunnel Supply 2 | 1.2 m
PF.5 | Ventilation Tunnel Extract 2 | 1.2 m
PF.6 | Ventilation Emergency Extract 2 | 1.2 m
PF.7 | Ventilation Service Cavern Supply | 1.1 m
PF.8 | Ventilation Service Cavern Extract | 1.1 m
PF.9 | Shaft Pressurisation | 1.2 m
PF.1
PF.4
PF.3
PF.6
PF.2
PF.5
PF.8
PF.7
PF.8
PF.1
PF.2
PF.3
PF.6
PF.4
PF.5
PF.9
PF.1
PF.2
PF.7
PF.8
PF.4
PF.5
PF.3
PF.6
Integration
under study
Tunnel Section
Shaft View

## Slide 10
2. Update on integration
Inigo Martin Melero (CERN/EN/CV)
10
Technical Areas in H,L | Air Supply | Extraction | Emergency extraction
Access Mode | Ventilation Service Cavern: 40,000 m3/h | 40,000 m3/h | 40,000 m3/h
RF Points: H, L
Reference | Duct Function | Size
PH.1 | Ventilation Service Cavern Supply | 1.1 m
PH.2 | Ventilation Service Cavern Extract | 1.1 m
PH.3 | Ventilation Klystron Gallery Supply | 1 m
PH.4 | Ventilation Klystron Gallery Extract | 1 m
PH.5 | Ventilation Klystron Gallery Emergency | 1 m
PH.6 | Ventilation Tunnel Supply 1 | 1.2 m
PH.7 | Ventilation Tunnel Extract 1 | 1.2 m
PH.8 | Ventilation Emergency Extract 1 | 1.2 m
PH.9 | Ventilation Tunnel Supply 2 | 1.2 m
PH.10 | Ventilation Tunnel Extract 2 | 1.2 m
PH.11 | Ventilation Emergency Extract 2 | 1.2 m
PH.12 | Shaft Pressurisation | 1.2 m
PH.12
PH.12
PH.9
PH.1
PH.2
PH.3
PH.4
PH.5
PH.6
PH.7
PH.8
PH.10
PH.11
PH.5
PH.7
PH.6
PH.4
PH.3
PH.2
PH.1
PH.9
PH.10
PH.8
PH.11
Integration
under study
Shaft View
PH.6
PH.6
PH.7
PH.3
PH.3
PH.9
PH.9
PH.11
PH.10
PH.4
PH.4
PH.8
PH.5
PH.5
Tunnel
Klystron Gallery

## Slide 11
2. Update on integration
Inigo Martin Melero (CERN/EN/CV)
11
Technical Areas in H,L | Air Supply | Extraction | Emergency extraction
Access Mode | Ventilation Service Cavern: 40,000 m3/h | 40,000 m3/h | 40,000 m3/h
RF Points: H, L
Reference | Duct Function | Size
PH.1 | Ventilation Service Cavern Supply | 1.1 m
PH.2 | Ventilation Service Cavern Extract | 1.1 m
PH.3 | Ventilation Klystron Gallery Supply | 1 m
PH.4 | Ventilation Klystron Gallery Extract | 1 m
PH.5 | Ventilation Klystron Gallery Emergency | 1 m
PH.6 | Ventilation Tunnel Supply 1 | 1.2 m
PH.7 | Ventilation Tunnel Extract 1 | 1.2 m
PH.8 | Ventilation Emergency Extract 1 | 1.2 m
PH.9 | Ventilation Tunnel Supply 2 | 1.2 m
PH.10 | Ventilation Tunnel Extract 2 | 1.2 m
PH.11 | Ventilation Emergency Extract 2 | 1.2 m
PH.12 | Shaft Pressurisation | 1.2 m
PH.12
PH.9
PH.1
PH.2
PH.3
PH.4
PH.5
PH.6
PH.7
PH.8
PH.10
PH.11
PH.6
PH.6
PH.7
PH.3
PH.3
PH.9
PH.9
PH.11
PH.10
PH.4
PH.4
PH.8
PH.5
PH.5
Tunnel
Klystron Gallery
Tunnel Section
Tunnel Section
Integration
under study
PH.9
PH.6
PH.7
PH.10
PH.8
PH.11
PH.5
PH.5
PH.9
PH.6
PH.3
PH.3
PH.4
PH.4

## Slide 12
2. Update on integration
Inigo Martin Melero (CERN/EN/CV)
12
RF Points: H, L
RF Areas in H, L | Air Supply | Extraction | Emergency extraction
Run & Access Mode | 30.000 m3/h | 30.000 m3/h | OFF
Emergency conditions | < 30.000 m3/h | < 30.000 m3/h | < 30.000 m3/h
Reference | Duct Function | Size
PH.1 | Ventilation Service Cavern Supply | 1.1 m
PH.2 | Ventilation Service Cavern Extract | 1.1 m
PH.3 | Ventilation Klystron Gallery Supply | 1 m
PH.4 | Ventilation Klystron Gallery Extract | 1 m
PH.5 | Ventilation Klystron Gallery Emergency | 1 m
PH.6 | Ventilation Tunnel Supply 1 | 1.2 m
PH.7 | Ventilation Tunnel Extract 1 | 1.2 m
PH.8 | Ventilation Emergency Extract 1 | 1.2 m
PH.9 | Ventilation Tunnel Supply 2 | 1.2 m
PH.10 | Ventilation Tunnel Extract 2 | 1.2 m
PH.11 | Ventilation Emergency Extract 2 | 1.2 m
PH.12 | Shaft Pressurisation | 1.2 m
PH.12
PH.9
PH.1
PH.2
PH.3
PH.4
PH.5
PH.6
PH.7
PH.8
PH.10
PH.11
PH.6
PH.6
PH.7
PH.3
PH.3
PH.9
PH.9
PH.11
PH.10
PH.4
PH.4
PH.8
PH.5
PH.5
Tunnel
Klystron Gallery
PH.8
PH.5
Klystron Gallery Section
PH.3
PH.6
PH.11
PH.5
Klystron Gallery Section
PH.3
PH.9
Integration
under study

## Slide 13
2. Update on integration
Inigo Martin Melero (CERN/EN/CV)
13
Exp. Points: A, D, G, J
Reference | Duct Function | Size
PA.1 | Ventilation Experimental Cavern, Supply | 1.2 m
PA.2 | Ventilation Experimental Cavern, Extract | 1.2 m
PA.3 | Ventilation Experimental Cavern, Gas Extract | 1.2 m
Exp. Areas in A,D,G,J | Air Supply | Regular Extraction | Gas Extraction
Run & Access Mode | 50.000 – 70.000 m3/h | 50.000 – 70.000 m3/h | OFF
Flushing Mode | 50.000 – 70.000 m3/h | 50.000 – 70.000 m3/h | OFF
Fire Emergency | Up to 70.000 m3/h | Up to 70.000 m3/h | OFF
Gas Emergency | 20.000 m3/h | OFF | 20.000 m3/h
PA.1
PA.2
PA.3
PA.3
PA.3
PA.2
PA.2
PA.1
PA.1
Integration
under study
Shaft View

## Slide 14
2. Update on integration
Inigo Martin Melero (CERN/EN/CV)
14
Exp. Points: A, D, G, J
Technical Areas in A,D,G,J | Air Supply | Extraction | Emergency extraction
Run & Access Mode | Fresh air UAs: 20,000 m3/h Ventilation Service Cavern: 40,000 m3/h | 60,000 m3/h | 60,000 m3/h
Reference | Duct Function | Size
PA.4 | Ventilation Service Cavern Supply + Fresh Air for UAs Supply | 1.3 m
PA.5 | Ventilation Service Cavern Extract + Fresh Air for UAs Extract | 1.3 m
PA.6 | Ventilation Tunnel Supply 1 | 1.2 m
PA.7 | Ventilation Tunnel Extract 1 | 1.2 m
PA.8 | Ventilation Emergency Extract 1 | 1.2 m
PA.9 | Ventilation Tunnel Supply 2 | 1.2 m
PA.10 | Ventilation Tunnel Extract 2 | 1.2 m
PA.11 | Ventilation Emergency Extract 2 | 1.2 m
PA.12 | Shaft Pressurisation 1 | 1.2 m
PA.13 | Shaft Pressurisation 2 | 1.2 m
PA.1
PA.2
PA.3
PA.4
PA.5
PA.6
PA.7
PA.8
PA.9
PA.10
PA.11
PA.12
PA.13
PA.4
PA.5
PA.6
PA.7
PA.8
PA.9
PA.10
PA.11
PA.12
PA.13
Integration
under study
Shaft View

## Slide 15
2. Update on integration
Inigo Martin Melero (CERN/EN/CV)
15
Exp. Points: A, D, G, J
PA.1
PA.2
PA.3
PA.4
PA.5
PA.6
PA.7
PA.8
PA.9
PA.10
PA.11
PA.12
PA.13
Reference | Duct Function | Size
PA.1 | Ventilation Experimental Cavern, Supply | 1.2 m
PA.2 | Ventilation Experimental Cavern, Extract | 1.2 m
PA.3 | Ventilation Experimental Cavern, Gas Extract | 1.2 m
Reference | Duct Function | Size
PA.4 | Ventilation Service Cavern Supply + Fresh Air for UAs Supply | 1.3 m
PA.5 | Ventilation Service Cavern Extract + Fresh Air for UAs Extract | 1.3 m
PA.6 | Ventilation Tunnel Supply 1 | 1.2 m
PA.7 | Ventilation Tunnel Extract 1 | 1.2 m
PA.8 | Ventilation Emergency Extract 1 | 1.2 m
PA.9 | Ventilation Tunnel Supply 2 | 1.2 m
PA.10 | Ventilation Tunnel Extract 2 | 1.2 m
PA.11 | Ventilation Emergency Extract 2 | 1.2 m
PA.12 | Shaft Pressurisation 1 | 1.2 m
PA.13 | Shaft Pressurisation 2 | 1.2 m
PA.6++
PA.6+
PA.7++
PA.7+
PA.8++
PA.8+
++
+
Integration
under study
Tunnel Section
Tunnel Section

## Slide 16
16
3. Update on tunnel concept
Supply air
Exhaust air
Underground
Surface
Chilled water
Supply
Return
AHUs
Fancoils
Shaft
Cavern
Chilled water
Supply
Return
TO CHILLERS
TO CHILLERS
Inigo Martin Melero (CERN/EN/CV)

## Slide 17
Inigo Martin Melero (CERN/EN/CV)
17
General Input data | 
Cross section area | 15.2 m2
Sector length | 11,396 m
Max. Temperature (running conditions) | 32oC (to be confirmed)
Max. dew point Temperature | 12oC (to be confirmed
Compartment Input data | 
Number of Compartments | 29
Compartment length | 400 m
Volume Compartment | 6,080 m3
Ventilation parameters | 
Normal operation air flow per sector | 2 x 27,000 m3/h
Flushing air flow (longitudinal) per sector | 100,000 m3/h
Air supply points per compartment | 4
Air flow per supply point (normal operation) | 474 m3/h
Time to complete air renewal (flushing) | 1.7 h
Maximum air speed (normal operation – flushing) | 0.5 m/s – 1.8 m/s
Cooling capacity in normal operation for DT = 15 K per sector | 271 kW
3. Update on tunnel concept
General parameters

## Slide 18
Inigo Martin Melero (CERN/EN/CV)
18
3. Update on tunnel concept
Semi-transverse
Run Mode  Machine is in operation
Access Modes  Maintenance / works are done in the tunnel

## Slide 19
Inigo Martin Melero (CERN/EN/CV)
19
3. Update on tunnel concept
Semi-transverse
Flushing Mode  Full air renewal between
Access and Run Modes

## Slide 20
Inigo Martin Melero (CERN/EN/CV)
20
3. Update on tunnel concept
Semi-transverse
Emergency Mode  Smoke & fire or helium leak scenario

## Slide 21
Inigo Martin Melero (CERN/EN/CV)
21
3. Update on tunnel concept
Longitudinal
Run Mode  Machine is in operation
Access Modes  Maintenance / works are done in the tunnel
Flushing Mode  Full air renewal between
Access and Run Modes
Advantages
- No slab duct needed
- Less and simpler controls (dampers,etc)
- More efficient overall, less pressure loss
Challenges
Degraded modes
Force needed to open compartment doors
Larger dampers at compartment walls

## Slide 22
Inigo Martin Melero (CERN/EN/CV)
22
3. Update on tunnel concept
Longitudinal
Emergency Mode  Smoke & fire or helium leak scenario

## Slide 23
Inigo Martin Melero (CERN/EN/CV)
23
3. Update on tunnel concept
Adaptation Run / Access  Emergency
(+)
(-)
Signs criteria
0 min
3 min
15 min
0 min
3 min
8 min
STABLE
VENTILATION
STABLE
VENTILATION
Emergency in central compartment*
Semi-transverse
Longitudinal
*With 7000 m3/h per affected compartment
SMOKE EXTRACTION CONDITIONS MET
SMOKE EXTRACTION CONDITIONS MET

## Slide 24
Inigo Martin Melero (CERN/EN/CV)
24
3. Update on tunnel concept
Adaptation Run / Access  Emergency
(+)
(-)
Signs criteria
0 min
3 min
15 min
0 min
3 min
8 min
Emergency in lateral compartment*
Longitudinal
Semi-transverse
*With 7000 m3/h per affected compartment
STABLE
VENTILATION
STABLE
VENTILATION
SMOKE EXTRACTION CONDITIONS MET
SMOKE EXTRACTION CONDITIONS MET

## Slide 25
Inigo Martin Melero (CERN/EN/CV)
25
3. Update on tunnel concept
Fire heat effects
(+)
(-)
Signs criteria
7000 m3/h per affected compartment
Considering heat release rate of fire
Inversion of the supply,
Smoke leaves fire-affected compartment
Prevention by increase in airflow
Local expansion of air due to fire heat
Semi-transverse
supply
7,000 m3/h
supply
14,000 m3/h
Longitudinal
Inversion of supply
Inversion of supply
supply
14,000 m3/h
supply
7,000 m3/h

## Slide 26
Inigo Martin Melero (CERN/EN/CV)
26
3. Update on tunnel concept
Pressure differences
(+)
(-)
Signs criteria
Access / Run
Flushing
Emergency, 1 compartment*
Emergency, 2 compartments*
Pressure drop across compartment walls with closed doors and opened emergency dampers: 93 Pa
Pressure drop across compartment walls with closed doors and opened emergency dampers: 36 Pa
Maximum admissible opening force < 70 N
*With 10,000 m3/h per affected compartment, and a damper of 0.6 m2
Required opening force = 87 N
Required opening force = 224 N
However, if damper increased to 1 m2, we are below < 70 N in both cases.

## Slide 27
3. Update on tunnel concept
Inigo Martin Melero (CERN/EN/CV)
27
Degraded modes
Cases
Longitudinal
Extraction Dampers
Wall Dampers
Semitransverse
Extraction Dampers
Emergency supply dampers
Normal Ventilation Dampers
Door
Door
Extraction dampers of adjacent and affected compartments do not open
The wall damper, open by default, closes.
Worst case: all dampers of affected and adjacent compartments close
The door does not close, it stays open
Extraction dampers of adjacent and affected compartments do not open
They don’t change position
They don’t open
Door does not close, it stays open
Supply from both extremes and no extraction will result in the tunnel being pressurized. There won’t be any flow, the smoke should behave as a case without any ventilation.
Asymmetric and incomplete smoke extraction.
Fire enclosed in the affected compartments by the walls. Depression created in the compartments, while pressure at door levels is much higher. Sliding door as pressure relief mechanism.
Compartmentalization is lost, but the smoke extraction would continue to work.
Affected and adjacent compartments are overpressured
Affected and adjacent compartments have higher flow than nominal values
The air supply will be smaller than in the nominal values. Smaller smoke extraction, slightly depressurized compartment.
Higher risk of smoke leaving the affected/adjacent compartments than in longitudinal.

## Slide 28
28
4. Next steps
Analyze and decide between the semi-transverse ventilation or changing to the longitudinal concept
Interact with the rest of departments and exchange information: heat loads, ducts integration, sustainability considerations…
Further refine the design of special areas like Klystron Galleries, connecting tunnels, etc.
Proceed with the preTDR tasks defined for the ventilation part
Inigo Martin Melero (CERN/EN/CV)

## Slide 29
Thank you for your attention.
Thank you for your attention.

## Slide 30
Thank you for your attention.
SPARES

## Slide 31
Inigo Martin Melero (CERN/EN/CV)
ThermoTun software
Metro Melbourne
Citytunnel Frankfurt
1D modelling software, developed by Dundee Tunnel Research and University of Dundee (Scotland).
Transitory analysis of air pressures and velocities.
Transient simulations

## Slide 32
Inigo Martin Melero (CERN/EN/CV)
Simulations
Both the baseline, semi-transverse concept and the alternative, longitudinal concept are included in the simulations.
Simulation of the Run Modes.
Supply fans ramp up time: 60 s
Setpoint in damper of baseline concept ramp up time: 100 s
Simulation of Emergency Modes.
Timeline of events for transition
from Run to Emergency Modes
Configuration

## Slide 33
Inigo Martin Melero (CERN/EN/CV)
Longitudinal ventilation
Pressure on compartment
door
Rectangular fire dampers with dimensions 1.5 m x 0.4 m (free area 0.6 m2) are considered, to be moved from robot space.
Pressure difference across compartment walls must not hinder the opening of integrated doors in case of emergency
Maximal door opening force of 70 N shall not be exceeded. Accounting for the type and dimensions of the doors in the compartment walls (swing door with dimensions 1.5m x 3.0m), the maximal allowable pressure difference is 30 Pa.