## Slide 1: Technical Galleries Consolidation Program
TG-CONS – SCE-SAM Heating network consolidation
Activities overview
Michela LAGIOIA Gregoire GUILLOT
30/05/2024`

## Slide 2: Overheated pipes – Past works
Gallery 835 South
Gallery 836
Gallery 825 Part 4.1
Gallery 825 – Part 4.1
836
835 South
WORKSITE COMPLETED IN 2023 AND 100% INVOICED
Gallery 835 North – Pilot gallery in 2022
835 North
ISR RING
RECENTLY RENOVATED

## Slide 3
2023: Summary of the activities
OLD CONFIGURATION
DISMANTLING
PIPE INSTALLATION
INSTALLATION OF INSULATION
ACTIONS IN EVERY GALLERY:
Asbestos removal campaign (SCE-CE)
Replacement of the pipes and insulation
Increase in the thickness of the insulation according to the current norms (SIA384-1 and Mopec 2018)
SCHEDULE
Heating stop: 01/05/23
Start of the activity: 15/05/23
End of the activity: 01/11/23
Heating start: 23/10/23
~600 m REPLACED PIPES
~24 tons OF EVACUATED PIPES & SUPPORTS
~22 tons OF INSTALLED PIPES & SUPPORTS
Notes: PICTURES

## Slide 4: Heating pipes Current projects
Gallery 825 Part 4.2
Gallery 826
Gallery 825 Part 4.2 – Summer 2024
From Building 35 to 110, branches included
Gallery 826 – Summer 2024
De-classification from superheated water to heated water
New Technical Specifications:
- Nominal Pressure PN 16
- Design Temperature 99◦C
Notes: FROM 125 C OF TEMP
PN 25 NOMINAL PRESSURE

## Slide 5: Heating pipes - Schedule 2024
Latest update:
Lockout ongoing
Insulation dismantling finished in 825.

## Slide 6: FUTURE WORKS
825 Part 3 – Year 2025-2026
Priority: to continue gallery 825, shadowing EN-CV
Budget constraints: the scope will be defined based on the budget availability of the project.
Collaboration with EN-CV.
821 TL4A– 2027
825 Part 2 – Year 2028-29