## Slide 1
PERLE
-
Cryogenics
P. DUTHIL (IJCLab/CNRS)
(on behalf of the PERLE’s team)
September 17th 2024

## Slide 2: Scope of Cryogenics
What to cool?
Cryomodule
Booster
PERLE ERL

## Slide 3: Scope of Cryogenics
Bi-phase pipe
(Ø=95.5 mm)
Niobium cavity
What to cool?
  The PERLE cryomodule
Some RF features | IJCLab series
Frequency | 801.58 MHz
Eacc | 22 MV/m
Lacc = (n../2) | 0.936 m
Q0 | 3·1010
R/Q0 @β=1 | 521 
PRF_diss_cav | 27 W @ T=2 K per cavity
    4x 5-cells SRF cavities
He vap. pumping
LHe II
T=2 K; P=31 mbar
LHe II Subatmospheric saturating bath
1300 mm
- Cavity: 48 kg of bulk niobium
- Helium tank:
  Tank: 37.7 kg of Ti grade 2
  Flanges: 3.7 kg of Nb-Ti
- Cryogenic vessel : VLHe=32.8 L
Max. Allowable Working Pressure PS=1.5 bar(g)
(art. 4.3 of Pressure Equipment Directive 2014/68/EU)
Ø=368 mm
Mechanical aspects:

## Slide 4: Scope of Cryogenics
What to cool?
  The PERLE cryomodule
    4x4x HOM couplers
4 HOM couplers per cavity
See C. BARBAGALLO’s talk
Cryogenic goals:
Remove heat induced by RF loading
Intercept heat flowing along the cables
Active cooling with LHe II TBC:
Pcooling~ 0.04 W per HOM coupler @ T=2 K
Probe design  LHe II cooling TBC
Hook design  LHe II cooling TBC
DQW design  LHe II cooling needed
(mech. and thermal designs ongoing)

## Slide 5: Scope of Cryogenics
What to cool?
  The PERLE cryomodule
Supercritical helium
(T=5 K, P=3 bar)
    4x RF power couplers double walls
Supercritical helium
T=300 K, P=3 bar
RF power coupler
Double wall
(supercritical helium flowing in channels)
See E. MONTESINO’s talk
Cryogenic goals:
Intercept heat flowing from room environment (diffusion + radiation)
Remove heat from RF dissipation along the double wall
Cooling mass flow rate: 0.2 g/s per coupler
(maximum preliminary estimate)
MB ESS RF power coupler
Cavity interface -

## Slide 6: Scope of Cryogenics
What to cool?
  The PERLE cryomodule
    5x HOMS Beam Line Absorbers
      3 between the 4 SRF cavities
      (and 2 warm at the end of the cryomodule)
See C. BARBAGALLO’s talk
Cryogenic goal: extract heat induced by RF dissipation (HOMs damping)
Foreseen (TBC):
- Main cooling: supercritical helium at T~60 K, 12.5 bara
- Heat intercept: supercritical heat at 5 K, 3 bara
Pcooling: ~200 W @ 60 K now considered for 5 absorbers
( to be evaluated; R&D ongoing)

## Slide 7: Scope of Cryogenics
What to cool?
  The PERLE cryomodule
    1x Thermal shield
Cooled with supercritical helium
(T~60 K, P=12.5 bar)
Pcooling: ~260 W @ 50 K
(based on ESS cryomodule measurements)
Cryogenic goals:
Reduce the heat which is radiated from the room environment to the cold mass
Intercept heat diffusing along cables, supports, etc.

## Slide 8: Scope of Cryogenics
What to cool?
  The PERLE SRF booster
Injection line
    String of cavities:
      4x SRF single-cell cavities @ 2 K with superfluid helium
      No HOM coupler
      4x RF power couplers with supercritical helium at 3 bara and from 5 to 300 K
    1x thermal shield with supercritical helium at 12.5 bara and at ~60 K
- Cavity: 12.4 kg of bulk niobium
- Helium tank: 23.4 kg of Ti grade 2
- Cryogenic vessel: VLHe=7.7 L
See R. ROUX’s and G. OLRY’s talks

## Slide 9: Scope of Cryogenics
How much to cool? Preliminary heat loads budget
ERL PERLE | Q @ 2 K | Q @ 60-70 K | LHe 5-300 K
 | (W) | (W) | (g/s)
Cryomodule |  |  | 
4x SRF cavity @Q0=3e10 | 108 |  | 
Cryomodule static | 25 |  | 
16x HOM Rfdyn | 0.64 |  | 
16x HOM static | 0.64 |  | 
4x RF power coupler | 1.5 |  | 0.8
Absorbers |  |  | 
Thermal shield + heat intercepts |  | 260 | 
Booster |  |  | 
4x SRF cavity @Q0=1e10 | 12 |  | 
Cryostat static | 25 |  | 
4x RF power coupler | 1.5 |  | 0.8
Thermal shield + heat intercepts |  | 175 | 
2x Valve Boxes | 15 | 50 | 
2x Cryolines | 15 | 30 | 
Beam losses | 10 |  | 
TOTAL | 210 | 515 | 1.6

## Slide 10: Scope of Cryogenics
How much to cool? Preliminary heat loads budget
  PERLE ERL:
  LINAC pattern:
Source
Booster
Cryomodule 1
Expérience
Dump
Cryomodule 2
Cryomodule 3
7MeV
89MeV
171 MeV
253 MeV
Cryogenics:
Pcryo 2 K: 515 W
Pcryo 60-70 K: 1 720 W
LHe: 3.2 g/s
Pelec: 462 kW
Source
Booster
Cryomodule
Expérience
Dump
7MeV
1st loop : 89MeV
2nd loop : 171 MeV
3rd loop : 253 MeV
Cryogenics:
Pcryo 2 K: 210 W
Pcryo 60-70 K: 515 W
LHe: 1.6 g/s
Pelec: 200 kW

## Slide 11: Scope of Cryogenics
How to cool?
  Currently: decommissioning of the BESSY VSR (Variable pulse length Storage Ring) refrigeration system located in Helmholtz-Zentrum Berlin (HZB)
  Cooperation agreement between HZB and IJClab set up for the transfer of the cryogenic refrigeration system to IJCLab by end of 2026 for PERLE operations
  This cryogenic refrigeration system
    includes:
      A Linde refrigerator: based on the refrigerator of CMTF at Fermilab, but 2 K production part is separated (in a distribution box)
      A distribution box (or valve box) producing superfluid helium
      A cryogenic transfer line (~30 m long) containing several cryogenic circuits
      Additional components: cycle compressors, helium pumping system, etc. (transfer to IJCLab is to be confirmed)
    specified and designed in two stages (steps): stage 1 = low power and stage 2 = high power refrigeration
    1st stage was installed in 2020
    1st stage was commissioned in 2022 (almost completely)
  NDA between IJCLab and Linde is being set up to ease communication on technical aspects
Temperature level Heat load | 1st stage
1.8 K (evaporation at 16.4 mbara) | 186 W
60 K (warming from 45 to 80 K at ~12.5 bara) | 1 300 W
4.5 K (liquefaction at 1.25 bara) | 2 g/s
eq. 207 W @ 2K
(210 W for PERLE’s heat budget; no margin)
515 W for PERLE estimates
~1.6 g/s for PERLE estimates

## Slide 12: Perspectives
How to cool?
Low pressure pumping stations
5 K, 3 bara
1.8 K
1.8 K
Distribution box
(Valve box)
Cold box
(cryogenic refrigerator)
Cryogenic transfer line
Cycle compressor
LHe
LN2

## Slide 13: Conclusion & Perspectives
Intense design work on the booster and cryomodule is currently ongoing
    cooling concepts for HOM couplers to be choosen
    more accurate numbers to be provided for heat loads
Conceptual design of the cryogenic distribution system
  Includes: transfer lines and distribution boxes
   ongoing and expected to be finalized by mid 2025
Opened questions:
  Cooling concept for BLAs in the cryomodule?
  Is fast cooling needed for cryomodules cavities?
  Refrigeration stage 2: needed, how, when, what cost?
Siting studies began to integrate cryogenic systems
(and related subsystems)
  HZB’s in-kind integration into PERLE’s pattern
  Prepare a financial application for the support
  of cryogenic infrastructures
  Prepare the 2nd stage phase

## Slide 14: Thank you for your attention
Special thanks to:
Sébastien BLIVET Sylvain BRAULT Patricia DUCHESNE
Gille OLIVIER