## Slide 1: EN-EL Power activities YETS24/25 & LS3 – ADTC meeting
Mickael Lonjon & Bruno SAINT SULPICE, on behalf of EN-EL
04/07/2024

## Slide 2
EN-EL tests
Projects
Timeline

## Slide 3: Tests

## Slide 4: Periodic safety activities on the power grid
Normal / Safety test
Auto transfer Test
AUG test PSB
Regulatory HSE inspection
Objective
Periodic testing and resolution of non-conformities
When :
During the RUN, YETS and LS
Constraints :
On a case-by-case basis
Objective
Verify the operation of the :
  16 generators
  17 Normal/Secured PLC’s
Carryout a power balance of the safety network
When :
During EYETS and each year of LS
Constraints :
Power outage for secured networks & General Service
One power outage per year from 6:00 to 6:10
Objective
Annually test all of CERN's AUG chains following the IS5.
Where
3 on Meyrin site,
7 on SPS,
3 on North Area,
When :
During YETS and at the beginning and at the end of LS
Co
nstraints :
Power outage for Secured, General Service, and Machine networks
1 day per test, from 6am to 8pm.
9 on LHC,
1 on Prévessin site
Objective
Test the Auto transfer system between France and Switzerland
When :
YETS24/25 & end of LS3 (after the SEM12 renovation)
Constraints :
Accelerators must stop operating.
Power usage is limited.
All General Service network refed from Machine networks for 4 days.
Periodic
activities

## Slide 5: Projects

## Slide 6: YETS24/25 – Projects/maintenance on AD
Replacement of 18kV protection relay network cards
  1 day of power outages, each load will be cut off for several minutes.
Installation and test of Local SCADA in ME49 (AD)
  2 days of testing with power outages for load reconfiguration.
Replacement of the low voltage switchboard EBD7*49  EBD1*49 + EBD11*49 in 2 steps (description below)
  Each load will be transferred to EBD1*49, resulting in a power outage of several hours per load.
Protection relay
Local Scada

## Slide 7: Low voltage AD network renewal (EBD1*49 & EBD11*49) :
Phase 1 : Installation of the new transformer and the new switchboard during the run, (October).
  Small false floor modification and cable trays installation (far from the converters)

## Slide 8: Low voltage AD network renewal (EBD1*49 & EBD11*49) :
  Phase 2 : Transfer of the loads and replacement of small loads switchboard
    Small powercuts (1/2 days) expected for all the services hall and control room equipments
    2 days of power cut for the small loads switchboard replacement
    Affects lighting and power sockets for the service hall + control room

## Slide 9: List of loads :
Cranes : PR190, PR191, PR192
CV equipments in 193, 195, 196 :
  Ventilation unit below the roof of the main hall
  Cooling unit in 193/R-410 (Longer power cut due to cable replacement 3 days)
  Ventilation room 193/R-403
Control room equipments :
  Lighting, Power sockets except EOD ones
Experimental Hall lighting, power sockets
  Small switchboard coming from ERD network not affected.
Satellite buildings general services 393, 196

## Slide 10: Timeline on AD

## Slide 11
2024
2025
TEST
Travaux ME49
2024
2025
Dec
Jan
Feb
15/12
22/12
Today
1.4 days
AUG (2 jours)
11 Jan - 12 Jan
0.3 wks
Test Auto-transfert (3 jours)
Jan 21 - Jan 23
8 Jan
Test Normal / Secours (10 min - 6h-6h10)
Jan 13 - Jan 14
2 days
Installation and test of Local SCADA
Jan 13
1 day
Remplacement des cartes réseaux des relais Arcteq (relais 18kV)
Dec 15 - Feb 15
9 wks
Remplacement EBD1*49 --> EBD7*49 (transfert de charges)
29/12
05/01
12/01
19/01
26/01
02/02
09/02
6.2 wks
Dec 29 - Feb 10
YETS24/25
AD Timeline

## Slide 12
Thank you…
EN-EL Power

## Slide 13: Spare slide

## Slide 14: EBD7*49 loads
Départ | Description | Départ | Description
EBD7.1.1*49 | DEPANNAGE DEPUIS ERD5.2.5*49 | EBD7.3.7*49 | RESERVE
EBD7.1.2*49 | RESERVE EQUIPEE | EBD7.3.8*49 | DESENFUMAGE BS ET HALL ARMOIRE CV UBD07*49 LOCAL 193/R-403
EBD7.1.3*49 | ALIM. EBD12*49 TABLEAU ECLAIRAGE HALL AD | EBD7.3.9*49 | REALIM. ESD1*49 BAT.193
EBD7.1.4*49 | RESEAU 1 ONDULEUR EBS71*49 | EBD7.4.1*49 | COFFRETS PRISES HALL SALLE DE CONTROLE + REUNION 193/R-008
EBD7.2.1*49 | PONT ROULANT 1 HALL AD PR190 | EBD7.4.11*49 | RESERVE EQUIPEE
EBD7.2.11*49 | ALGECO BATIMENT 93 EBD1*49A TRANCHE 2 | EBD7.4.2*49 | BS REFROIDISSEMENT COFFRETS PRISES LOCAL REFROIDISSEMENT 193/R-410
EBD7.2.2*49 | PONT ROULANT 2 HALL AD PR191 | EBD7.4.3*49 | BS EQUIPEMENT COFFRETS PRISES FAUX PLANCHER CELLULES HT LOCAL 193/E-405
EBD7.2.3*49 | ALIM EBJ18*49 193/R-415 | EBD7.4.4*49 | PRISE 75A PILIER 3 DERRIERE LASER ASACUSA 193/SJ11
EBD7.2.4*49 | ALI. COFFRET DTU HHAAS-0096 | EBD7.4.5*49 | ALIM. EBD13*49 SALLE CONTROLE EXTERIEUR BATIMENT 93 (TRANCHE 1) + STAR POINT
EBD7.2.5*49 | PRISES FORCE GALERIE TECHNIQUE TP9 + PUISARD DP76 | EBD7.4.6*49 | COFFRET SUR FAÇADE ENTRE PORTES 305 ET 323 (COTE CENTRE DE CALCUL 513)
EBD7.2.6*49 | PONT ROULANT PR192 LOCAL 193/R-407 | EBD7.4.7*49 | HALL COFFRETS PRISES 2 ZONE ATRAP 193/S3-B193
EBD7.2.7*49 | T-INJECTION MUR BLINDAGE | EBD7.4.8*49 | HALL COFFRETS PRISES 3
EBD7.2.8*49 | MERIT DCCT 7000A | EBD7.4.9*49 | ALIM EBD11*49 LOCAL 193/R-407
EBD7.2.9*49 | BARRAQUE 6503 DEPART COMDAMNE | EBD7.5.6*49 | ALIM. EBD15*49 (PASSARELLE ASACUSA)
EBD7.3.1*49 | VENTILATION 1 COTE JURA ARMOIRE CW2 369 ET CW2 370 D PLATEFORME | EBD7.5.7*49 | ARMOIRE CW2 376 CLIM. SOUS STATION ELEC. 193/E-406 (ACCES DEPUIS 193/R-410)
EBD7.3.11*49 | ALIM. EBD1*49C BATIMMENT 393 | EBD7.5.8*49 | BS CONTROLE CLIMATISATION ARMOIRE CV UBD09*49 LOCAL 193/R-403
EBD7.3.2*49 | VENTILATION 2 COTE SALEVE ARMOIRE CW2 373 ET CW2 374 HALL AD PLATEFORME | EBD7.5.9*49 | RESEAU 2 ONDULEUR EBS71*49
EBD7.3.3*49 | VENTILATION 3 COTE JURA ARMOIRE CW2 367 ET CW2 368 HALL AD PLATEFORME | EBD7.6.1*49 | ALIM. ARMOIRE UIAC-00316
EBD7.3.4*49 | VENTILATION 4 COTE SALEVE ARMOIRE CW2 371 ET CW2 372 HALL AD PLATEFORME | EBD7.6.2*49 | RESERVE EQUIPEE
EBD7.3.5*49 | RESERVE | EBD7.6.3*49 | ALIM. EBD14*49D
EBD7.3.6*49 | ARMOIRE CW2 375 REFROIDISSEMENT AD LOCAL 193/R-410 | EBD7.6.4*49 | ALIM. ARMOIRE UIAC-00315

## Slide 15: EBD11*49 loads
Départ | Description | Départ | Description
EBD11.21*49 | RESERVE | EBD11.C13*49 | CDE SALLE DE CNTROLE C13
EBD11.23*49 | RESERVE (REPERE E23) | EBD11.C16*49 | CDE. ECL. ESCALIER C16
EBD11.25*49 | RESERVE (REPERE E25) | EBD11.C18*49 | CDE. ECLAIRAGE FAUX PLANCHER
EBD11.26*49 | ALIM. REGLETTE PC ECRAN 193/R-005 | EBD11.C27*49 | ALIM DP68 PUISARD STATION FLUIDE BA193 R-010
EBD11.33*49 | CHAUFFE EAU 193/R-102 | EBD11.C29*49 | RESERVE
EBD11.34*49 | ALIM. REDRESSEUR EBU11.34*49 | EBD11.C30*49 | RESERVE
EBD11.35*49 | ALIM. COFFRET EBJ14*49 BAT 493/E-404 | EBD11.C31*49 | CHAUFFE-EAU / PLAQUE CHAUF.
EBD11.36*49 | ALIM. REGLETTE 5PC SALLE CONTROLE 193/R-005 | EBD11.C7*49 | CDE. SALLE EQUIPEMENT
EBD11.37*49 | ALIM. REGLETTE 5PC SALLE CONTROLE 193/R-005 | EBD11.E1*49 | ECL. SALLE REFROID. 1.3.5
EBD11.A*49 | ARRIVEE DEPUIS EBD7.4.9*49 | EBD11.E13*49 | SALLE DE CONTROLE
EBD11.C1*49 | CDE SALLE REFROIDISSEMENT | EBD11.E14*49 | SALLE DE CONTROLE