## Slide 1: Reliability studies on uQDS, PDSU and PDSU-BIS interface for the IT protection
L. Felsberger, D. Westermann, D. Wollmann
Acknowledgements to R. Denz, C. Martin, T. Podzorny, I. Romera Ramirez, J. Steckert, J. Uythoven

## Slide 2: Introduction
Universal Quench Detection System (uQDS):
  Detect magnet quench
  Trigger PDSU
  Trigger FPA loop, Diagnostics
Protection Device Supervision Unit (PDSU):
  (Re-)Trigger magnet protection systems
  Trigger beam dump
  Detect spurious magnet protection firing
  Trigger FPA loop, Diagnostics
Beam Interlock System (BIS):
  Transmit beam dump request
  Diagnostics
Main failure modes:
  Missed magnet protection and beam dump (target for LHC systems - 1 in 1000 years)
  Spurious magnet protection and beam dump (target for LHC - 1 in 1 year)
Q1,Q2,Q3,BB,SCL
PCs
IT IP
uQDS
PDSU
Heaters + CLIQ
BIS
LBDS
PIC
IT protection systems study (CLIQ & HDS)
PICv2 reliability study
IT interlock panel (EPC interface)
BISv2 reliability study
This presentation
 Reliability analysis crucial
Accelerator Risk Matrix for LHC:

## Slide 3: Reliability Analysis Methodology
Top-Level Failure Modes, Effects and Criticality Analysis (FMECA)
Identify system, functions, associated risks and hazards and possible end-effects
Accelerator Risk Matrix
Quantify reliability requirements to mitigate risks and hazards
Top-Down reliability model
Capture system structure, redundancies, critical/non-critical parts, demand, inspection rates
Component-Level FMECA
Analyse detailed sub-system design to identify their failure probabilities for each end-effect
 Design qualification
Feed results from Component-Level FMECA into Top-Down FTA to qualify design or require design improvements
  Risk identification and quantification
  Risk estimation and mitigation

## Slide 4: Top-Down Reliability Model - Quench
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS

## Slide 5: Top-Down Reliability Model - Quench
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Magnet quench

## Slide 6: Top-Down Reliability Model - Quench
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Magnet quench
uQDS detection

## Slide 7: Top-Down Reliability Model - Quench
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Magnet quench
uQDS detection
6 PDSUs triggered

## Slide 8: Top-Down Reliability Model - Quench
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Magnet quench
uQDS detection
6 PDSUs triggered
Beam dump & magnet protection activated

## Slide 9: Top-Down Reliability Model - Quench
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Magnet quench
uQDS detection
6 PDSUs triggered
Beam dump & magnet protection activated
PC stopped (beam dump via PIC not fast enough)
Notes: Is a design choice to have the PIC too slow – could delay the uQDS to PDSU triggering protection to allow enough time for PIC – currently not done in favour of magnet protection – and probably we would not protect magnet fast enough

## Slide 10: Top-Down Reliability Model – Spurious Firing
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Spurious CLIQ/HDS firing

## Slide 11: Top-Down Reliability Model – Spurious Firing
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Spurious CLIQ/HDS firing
PDSU detects

## Slide 12: Top-Down Reliability Model – Spurious Firing
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Spurious CLIQ/HDS firing
PDSU detects
PDSU A/B retriggering
Beam dump and magnet protection request

## Slide 13: Top-Down Reliability Model – Spurious Firing
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Spurious CLIQ/HDS firing
PDSU detects
PDSU A/B retriggering
Beam dump and magnet protection request
PC stopped (beam dump via PIC not fast enough)
See also talks by C. Hernalsteens and T. Podzorny

## Slide 14: Top-Down Reliability Model – Spurious Firing
UR
Tunnel
USC/UJ
Q2a
Q2b
8 x HDS
8 x HDS
Q3
16 x HDS
16 x HDS
2x CLIQ Q1
2x CLIQ Q2
2x CLIQ Q3
UQDS Sc link B
PC
Interlock loop (FPA)
Beam abort requests to BIS
UQDS Sc link A
Interface Box
Q1
PDSU Q1 A
PDSU Q1 B
UQDS Q2 B
UQDS Q1 A
PDSU Q2 B
UQDS Q1 B
PDSU Q3 B
UQDS Q2 A
UQDS Q3 A
PDSU Q2 A
PDSU Q3 A
UQDS Q3 B
PIC
UQDS BB A
UQDS BB B
Courtesy of J. Spasic
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Spurious CLIQ/HDS firing
PDSU detects
PDSU A/B retriggering
Beam dump and magnet protection request
For magnet protection, uQDS provides additional redundancy.
But beam dump via uQDS detection not fast enough!

## Slide 15: Top-Down Reliability Models
Magnet Protection
Beam Dump/Spurious Firing
Magnet protection model ignores beam dump functionality (covered in spurious firing model)
Spurious firing model ignores magnet protection functionality (covered in magnet protection model)
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS

## Slide 16: uQDS & PDSU Hardware
uQDS and PDSU share designs of hardware modules
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Passive Mid-Plane
Monitoring Channel
Monitoring Channel
…
Monitoring Channel
Monitoring Channel
PSU
PSU
Digital Platform (FPGA)
Triggers
I/O
Interlocks

## Slide 17: uQDS & PDSU Hardware
uQDS and PDSU share designs of hardware modules
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Passive Mid-Plane
Monitoring Channel
Monitoring Channel
…
Monitoring Channel
Monitoring Channel
PSU
PSU
Digital Platform (FPGA)
Triggers
I/O
Interlocks

## Slide 18: uQDS & PDSU Hardware
uQDS and PDSU share designs of hardware modules
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Passive Mid-Plane
Monitoring Channel
Monitoring Channel
…
Monitoring Channel
Monitoring Channel
PSU
PSU
Digital Platform (FPGA)
Triggers
I/O
Interlocks

## Slide 19: uQDS & PDSU FMECA
uQDS and PDSU share designs of hardware modules
Detailed FMECA carried out for
  Analogue monitoring channels (similar between uQDS and PDSU)
  Digital Platform (identical between uQDS and PDSU)
  Approximate (pessimistic) FMECA for other modules & interfaces
Relevant failure mode types for magnet protection & beam dump
  Blind unsafe failure (detected upon commissioning or demand)
  Blind unsafe failure (detected every fill/ramp)
  Detected unsafe failure (visible in supervision)
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Passive Mid-Plane
Monitoring Channel
Monitoring Channel
…
Monitoring Channel
Monitoring Channel
PSU
PSU
Digital Platform (FPGA)
Triggers
I/O
Interlocks
0 FITS
0 FITS
16.7 FITS
11.4 FITS per channel
4.0 FITS
9.9 FITS/path
HDS/CLIQ CT/IFS/interface box
20.0 FITS/channel (to uQDS)
BIS concentrator
17.3 FITS/path
FITS: Failures in 10^9 hours (~10^5 years)
Notes: Note that PDSU test mode overwriting normal operational mode is crucial, otherwise HDS/CLIQ won’t trigger

## Slide 20: uQDS & PDSU FMECA
uQDS and PDSU share designs of hardware modules
Detailed FMECA carried out for
  Analogue monitoring channels (similar between uQDS and PDSU)
  Digital Platform (identical between uQDS and PDSU)
  Approximate (pessimistic) FMECA for other modules & interfaces
Relevant failure mode types for magnet protection & beam dump
  Blind unsafe failure (detected upon commissioning or demand)
  Blind unsafe failure (detected every fill/ramp)
  Detected unsafe failure (visible in supervision)
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Passive Mid-Plane
Monitoring Channel
Monitoring Channel
…
Monitoring Channel
Monitoring Channel
PSU
PSU
Digital Platform (FPGA)
Triggers
I/O
Interlocks
0 FITS
0 FITS
9.9 FITS/path (to PDSU)
16.7 FITS
0 FITS per channel (BB & SCL)
11.4 FITS per channel (BB & SCL)
4.0 FITS (BB&SCL)
Voltage taps, IFS, patch panel
13.8 FITS/channel (BB, SCL)
FITS: Failures in 10^9 hours (~10^5 years)
11.4 FITS per channel (coils)
0 FITS per channel (coils)
4.0 FITS (coils)
Voltage taps, IFS, patch panel
13.8 FITS/channel (coil)
Notes: Double check with Jens which of the blind failures in channel can be detected during magnet ramp

## Slide 21: uQDS & PDSU FMECA
Component failure rate source is 217+ electronics reliability prediction & FMD91/2016 standard
  Values apply for indoor, stationary mission profile during useful lifetime
If end effect unclear, pessimistic choice taken
Certain end effect assignments should be validated by functional tests in hardware
  E.g. behavior under 3.3V voltage rail drift, ADC behavior under reference voltage drift
FMECA process identified parts of design that may be optimized further for QDS CONS design for main dipole magnets
  E.g. placement of additional pull up/down lines in channel
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
FITS: Failures in 10^9 hours (~10^5 years)
Passive Mid-Plane
Monitoring Channel
Monitoring Channel
…
Monitoring Channel
Monitoring Channel
PSU
PSU
Digital Platform (FPGA)
Triggers
I/O
Interlocks
0 FITS
0 FITS
9.9 FITS/path (to PDSU)
16.7 FITS
0 FITS per channel (BB & SCL)
11.4 FITS per channel (BB & SCL)
4.0 FITS (BB&SCL)
Voltage taps, IFS, patch panel
13.8 FITS/channel (BB, SCL)
11.4 FITS per channel (coils)
0 FITS per channel (coils)
4.0 FITS (coils)
Voltage taps, IFS, patch panel
13.8 FITS/channel (coil)
Notes: Test mode PDSU – how to make sure it trggers when outside test mode

## Slide 22: Top-Down Reliability Model – Magnet Protection
UQDS
x6
PDSU
x2
x2
x2
1oo1 v 7oo8
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Complexity of model required making pessimistic simplifications
  Comparison with full redundancy structure confirmed that error is tolerable
Heaters & CLIQ modeled previously in IT protection systems study
Notes: System is so complex that conservative simplifications were made
  Series configuration of uQDS and PDSU triggers is assumed instead of respective redundancy  pessimistic
  Retriggering of PDSUs omitted
  Pessimistic assumptions on quench detection scenario

## Slide 23: Top-Down Reliability Model – Beam Dump/Spurious Firing
BIS
Concen-trator
Digital Platform
Beam dump trigger
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Channel
HDSCLIQ
(retriggered) Digital Platforms
Few pessimistic simplifications required
HDS case shown, as CLIQ has additional redundancy in read-out
  Clear separation of redundant paths as PDSU retriggering does not re-trigger between paths A & B
BIS concentrator
  New CIBFX design
  Originally developed for EPC use cases
  Reliability study as part of BISv2 reliability study
Notes: Remove CIBF
Discuss CIBFx – started for EPC, already have separate use, little pop-up
Hier sind die trigger zwischen den digital platforms nicht ersichtlich

## Slide 24: Results – Failure Rates
Maximum number of failures when the demand interval approaches the commissioning interval
  Magnet protection less reliable, mainly due to longer chain of systems in critical path
For both protection functions the reliability target is comfortably met.
  But under the condition of regular systematic testing
Repair/Inspection Policy:
Commissioning: 1 operational (op) year = 7200 hours/300 days
Ramp detection interval: 12 hours
Reaction to Supervision: 12 hours
Magnet protection: 128 instances that can have a single quench
Beam dump: 216 instances that can have a spurious trigger
1 spurious firing per year =
1 spurious firing every 216 op years
10 quenches every op year =
1 quench/coil every 12.8 op years
Target
Magnet protection
Beam dump
Chart: Failures per 1000 years in all ITs for different demand rates
| 1E-3 | 0.01 | 0.1 | 1 | 10 | 100 | 1000
 | 0.00016673 | 0.00057152 | 0.0051674 | 0.012799 | 0.0012799 | 0.00012799 | 1.2799e-05
 | 4.4409e-05 | 0.00013075 | 0.0011232 | 0.0027682 | 0.00027682 | 2.7682e-05 | 2.7682e-06
Notes: Wir haben 4 IT circuits, mit jeweils 6 Magnethälften und in jeder magnethälfte haben wir 4 Coils. Das macht 464= 96. Bezüglich der Busbars nehmen wir zwischen den Hälften eines magneten 1 busbar an (3 je circuit), eine zwischen den drei magneten und eine vom ciruict weg und hin. Also insgesamt 6 pro circuit und damit insgesamt 24 stück. FÜR sc link sagten wir 2 je circuit was 8 macht. Damit haben wir 96 coils die quenchen können und busbar plus sc link macht 32. Damit kommen wir auf 128.

## Slide 25: Commissioning interval Magnet protection
Chart: Failures per 1000 years in IT systems for different demand intervals
| 1E-3 | 0.01 | 0.1 | 1 | 10 | 100 | 1000
3 years | 0.00060857 | 0.002086 | 0.018861 | 0.18657 | 0.062062 | 0.0062062 | 0.00062062
1 year | 0.00016673 | 0.00057152 | 0.0051674 | 0.012799 | 0.0012799 | 0.00012799 | 1.2799e-05
With a commissioning interval of 3 years instead of 1 year, the number of failures increase
  Mainly due to the probability of blind failures accumulating that are only visible in commissioning or on demand.
    Difference smaller if demand rate is higher
With 3-year intervals, the reliability target is not met
Yearly quench test is recommended
Repair/Inspection Policy:
Commissioning: 1 or 3 operational years
Ramp detection interval: 12 hours
Reaction to Supervision: 12 hours
Magnet protection: 128 instances that can have a single quench
Beam dump: 216 instances that can have a spurious trigger
Target
10 quenches every op year =
1 quench/coil every 12.8 op years
Notes: If we can test even more during ramp – do it
Add requirements

## Slide 26: System Monitoring & Testing Magnet protection
Chart: Failures in 1000 years - Magnet protection - demand every 12.8 years - different fill inspection intervals
| 12 hours | 72 h (0.01 op years) | 720 h (0.1 op years) | 7200 h (1 op year)
ramp detection & reaction to supervision | 0.0009999 | 0.0010112 | 0.65016 | 0.68173
Strong impact of less frequent/imperfect testing
  Only a small increase of about 1.1E-05, if the failures are detected and repaired after 72 hours.
  Maximum of 6.8E-01 failures if the failures are detected for the first time during yearly commissioning.
    This assumes an interlock of operation (SIS) if both critical paths lose supervision.
Monitoring & ramp testing is crucial for protection function!
  Extending coverage yields additional reliability margins
Detected problems can be fixed after fill
  Do not need to stop operations
Repair/Inspection Policy:
Commissioning: 1 operational (op) year
Ramp detection interval: 12 hours  7200 hours
Reaction to Supervision: 12 hours  7200 hours
Magnet protection: 128 instances that can have a single quench
Beam dump: 216 instances that can have a spurious trigger
Target
Notes: This assumes an interlock of operation (SIS) if both critical paths lose supervision. This only becomes relevant though when the test execution/repair interval is close to 7200 hours. Without it, values would be 10% higher.

## Slide 27: Conclusions & Next Steps
A reliability model for the quench protection and beam dump functions of the IT shows
  The foreseen uQDS, PDSU and BIS concentrator hardware design conforms with the reliability requirements
  This is under the condition that
    yearly commissioning tests are performed (IST) to check the integrity of the system and all interfaces
    an automated test during ramp is executed every LHC fill as part of a sequencer task to check integrity of the system
Follow-up of the study
  The uQDS/PDSU FMECA analysis results should be validated by selected HW functional tests/simulations
  Availability aspects of the system to be quantified and checked against operational data
  An analysis of critical firm- and software and configuration management should complement the hardware study
In view of the consolidation of the LHC main dipole QDS system
  The reliability model should be adapted, and pessimistic assumptions refined
  Design improvements triggered by uQDS/PDSU FMECA analysis should be implemented if possible

## Slide 29: Protection System Life Cycle
Machine Protection systems development follows defined life-cycle
Ensures that risks are mitigated
Inspired by IEC 61508 and adapted for CERN context
The scope of the uQDS & PDSU reliability analysis is to
  Identify risks and hazards and quantify requirements for their mitigation
  Qualify the detailed hardware design according to the defined requirements
  Clear and exhaustive specifications of the project
  Thorough risk and hazards analysis, definition of safety requirements
  Testing and validation
  Commissioning of the system
  Procedures
  Experts’ advice
  Trainings
  Operation and maintenance
  Periodic testing
  Design of the system
  Reliability analysis
  Availability
  Dependability
Courtesy of M. Kalinowski

## Slide 30: Component-Level FMECA - Introduction
Failure Modes, Effects, and Criticality Analysis (FMECA)
Purpose: identify potential failure modes of individual components within a system & quantify failure impact at system level
Id | Component | Description | failure_mode | Alpha | Component Failure Rate | Failure Mode Rate | End Effect
1.1 | C2 | ¬±10% 50V X7R SMD Multilayer Chip Ceramic Capacitor | Open | 9 | 0.357 | 0.032 | Spurious Protection
1.1 | C2 | ¬±10% 50V X7R SMD Multilayer Chip Ceramic Capacitor | Parameter change | 61 | 0.357 | 0.218 | No effect
1.1 | C2 | ¬±10% 50V X7R SMD Multilayer Chip Ceramic Capacitor | Short | 30 | 0.357 | 0.107 | Blind channel

## Slide 31: FMECA Process Key steps
Using Bill of Materials, do a component-wise Failure Rate Prediction.
  Mainly based on 217Plus standard (2015/RIAC, but also available: Telcordia TR/SR, MIL-217, NSWC). Completed by manufacturer and test data.
  Requires definition of mission profile/environment as well as operating conditions for individual components
Identification & apportionment of component failure modes
  i.e., capacitor -> {open, param. change, short}.
  Based on handbooks (MIL-HDBK338, FMD2016).
Assigning end-effects to each failure mode of every component of the system.
  i.e., Capacitor C1: open -> no effect, short -> false dump, param. change -> blind failure.
Screenshot of Isograph Reliability Workbench (tool used for FMECA analysis)

## Slide 32: Top-Down Reliability Model – Magnet Protection
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Reliability model assumes single coil quench
Quench protection strategy is inherently redundant
For single coil quench, triple redundant detection method & each of them redundant in hardware

## Slide 33: Top-Down Reliability Model – Magnet Protection
Pessimistic scenario
Q1,Q2,Q3,BB,SCL
uQDS
PDSU
Heaters + CLIQ
BIS
Reliability model assumes single coil quench
To reflect that symmetric quenches can occur, which have reduced redundancy, two of three redundant paths are omitted.
Quench protection strategy is inherently redundant
For single coil fault, triple redundant detection method & each of them redundant in hardware

## Slide 34: CIBFx+CIBF or only CIBFx?
Depending on the demand rate, the additional CIBF reduces the number of faults per 1000 years by 0 to 2.20E-05.
In the relevant range of 0.0046 spurious firings per year per HDS/CLIQ (1 spurious firing per year), the influence is with a difference of about 3.24E-08 to 3.24E-09 almost negligible.
Chart: Failures in 1000 years - Beam Dump/Spurious Firing with and without CIBF
| 1E-3 | 0.01 | 0.1 | 1 | 10 | 100 | 1000
with CIBFx and CIBF | 2.2744e-05 | 5.6534e-05 | 0.00045919 | 0.0011252 | 0.00011252 | 1.1252e-05 | 1.1252e-06
only CIBFX | 4.471e-05 | 6.4035e-05 | 0.00046575 | 0.0011285 | 0.00011252 | 1.1285e-05 | 1.1285e-06

## Slide 35: Design qualification – Analytic Approach – Magnet Protection
An analytical approach was chosen over a simulation approach for time reasons and results are consistent
The minimal cut set method was used to consider various inspection intervals and repair actions
Chart: Monte Carlo simulation (Availsim4) vs Analytic model Inspection interval: 1 year
| 7.2 | 72 | 720 | 7200 | 72000 | 720000
Availsim4 | 10.01 | 60 | 283.5 | 364.2285 | 51.7535 | 5.7214
Analytic model | 1.7617 | 17.6144 | 175.8451 | 436.3023 | 43.6302 | 4.363