## Slide 1: Cooling and ventilation studies
F. Dragoni, N.Zaric/ EN-CV , HI-ECN3 WP4 – TARGET COMPLEX #2 – 28.06.2024.

## Slide 2: Agenda
BA82 Building:
  Current cooling stations
  Current ventilation system
Status of User’s requirements on cooling:
  Informations we have / Missing informations
Target – Helium Station Gas:
  Gas Circulation Skid
28/06/2024
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691

## Slide 3: BA82 building: Current cooling station
North area cooling capacity:
  Primary water:
    Nominal cooling capacity: 33MW
    Max cooling capacity: 45MW
    Bld 893, 4 cells
    Nominal flow rate: 2100m3/h
  Demineralized water:
    3 cooling plants for underground halls and tunnels located in BA80, BA81 and BA82
      BA80: TTC2, TDC2, TT20 – 10MW, 675m3/h
      BA81: TT83, TT84, EHN1 – 15MW, 900m3/h
      BA82: EHN2, ECN3, GHN 300, NA62, TCC8 – 7MW, 450m3/h
        Rectifier cooling circuit (Hall 891) – 0.2MW, 17m3/h
  Chilled water:
    Used for air-conditioning of the buildings, tunnel, computer rooms and halls
    Production station in BA81 consists of 3 water cooled chillers, cooling capacity 3 x 2.2MW (N+1 redundancy)
28/06/2024
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691

## Slide 4: BA82 building: Current cooling station
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024

## Slide 5: BA82 building: Current cooling station
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024
Demineralized water for power converters
Demineralized water – supply for Amber, EHN2, NA62, ECN3, TCC8
MIXED water – supply for EHN2
Chilled water from BA81
Raw water from CT2

## Slide 6: BA82 building: Current cooling station
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024
BA82 Users:
  Demineralized water:
    Magnets
    Water cooled cables
    Power converters
    Vacuum pumps
  Chilled water:
    2 old AHUs
    1 new AHU
    Clean room AHU
  Mixed water production

## Slide 7: BA82 building: Current cooling station
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024
Demineralized water – Now

## Slide 8: BA82 building: Current cooling station
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024
Demineralized water – Future

## Slide 9: BA82 building: Current cooling station
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024
Magnets

## Slide 10: BA82 building: Current cooling station
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024
Demineralized water – Nominal values
Demineralized water - Future
Current measurement: Cooling capacity: 6.2MW Flow rate: 290 m3/h
Chilled water – to be clarified Mixed water needs – no need so far
Pending final verification BA82 stations for EHN2, TCC8 and ECN3 have sufficient power and flow rate
 | Tin | Tout | Pmax | Pressure drop | Total dissipated Power | Total flow | Type of water
 | (°C) | (°C) | (bar) | (bar) | (kW) | (m3/h) | 
Magnets | 26 | 35-42-46-56 | 30 | 15 | 696.4 | 77.8 | Demineralized
Power converters | 26 | 36 | 16 | 3 | 45 | 2 | Demineralized
Vacuum pumps |  |  |  |  | 4.19 | 0.363 | Demineralized
Water cooled cables |  |  |  |  | 200 | 17.3 | Demineralized
EHN2/Amber facility |  |  |  |  | 4000 | 105 | Demineralized
 |  |  |  | Σ | 4945.59 | 202.46 | 
 |  | Tin | Tout | Pmax | Pressure drop | Total dissipated Power | Total flow | Type of water
 |  | (°C) | (°C) | (bar) | (bar) | (kW) | (m3/h) | 
1st cooling substation | Power converters | 26 | 36 | 16 | 3 | 165 | 22.56 | Demineralized
2nd cooling substation | Vacuum pumps |  |  |  |  | 4.19 | 0.363 | Demineralized
 | SHIP |  |  |  |  | 1166 | 99.17 | Demineralized
 | Water cooled cables |  |  |  |  | 200 | 17.3 | Demineralized
 | EHN2/Amber facility |  |  |  |  | 4000 | 105 | Demineralized
3rd. 4th, 5th cooling substation | Target complex | 27 | 30-33.7-35.6 |  |  | 380 | 65.76 | Demineralized
 |  |  |  |  | Σ | 5915.19 | 310.15 | 

## Slide 11: Ventilation system – New service building
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024
In progress – will be shown in presentation of New service building (presentation later afternoon)

## Slide 12: Target - Helium Station Gas
Market survey activity – Technical selection
Compressor :
  Aerzen
  Roots UK
  Linde
Heat Exchanger
  Funke (n_TOF HX)
  VDL
  ETS
Filter
  Porvair Filtration (Nuclear)
  Guerin Filter
Water station 45 m3/h @ 18 bar (g) – 37 kW motor – 250 motor size
Helium compressor 8050 Nm/3h @1.5 to 5 bar(g) – 630 kW motor – 400 motor size
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024

## Slide 13: Gas Circulation Skid
Compact design for Nitrogen erosion skid on lead blocks carried out in 2018
Requested update pump curve for helium
Possibility of having safety diaphragm and increased gas tightness
Cold source was stand-alone chiller need to be converted to different chilled
F. Dragoni, N.Zaric | Cooling and ventilation studies| Indico 1426691
28/06/2024