## Slide 1: ARC cryogenic capacity in the HL-LHC era
Benjamin Bradu
(TE-CRG)
228th HiLumi WP2 Meeting – 02/07/2024

## Slide 2: Content
Cryo infrastructures evolutions for HL-LHC
Consequences for the ARC beam screen cryo capacities
What will happen after LS3 for LHC cryogenics ?
BST project
Conclusion

## Slide 3: Cryo infrastructures evolutions for HL-LHC (reminder)
LHC cryogenics today
Non Hilumi sectors (LL) : S23, S34, S67, S78
  No changes in cryogenics infrastructures (cryoplants “A” )
  PS: the cryoplant “A” for S34 was already upgraded during LS2 for HiLumi
Hilumi sectors (HL) : S12, S45, S56, S81
  Existing cryo infrastructures (cryoplants “B”) remains but…
  The IT + DFBX + D2 + associated QRL removed until Q4
   capacity recovery in the existing cryoplants “B” !
  2 new cryoplants at P1/P5 will be installed
    Will manage the future IT+CP+D1+DFX+DFM+D2+CC
    (not discussed in this presentation)
New cryoplant
New cryoplant
Handled by
new cryoplants
Remain attached
to existing cryoplants “B”

## Slide 4: Consequences for the ARC cryo capacities
LHC cryoplants are supplying many devices in parallel at different temperatures
  Thermal shields between 50 K and 75 K
  Main superconducting magnets at 1.9 K (ARC dipoles/quadrupoles)
  Stand Alone superconducting magnets at 4.5 K (D3, Q4, Q5, Q6)
  RF cavities at 4.5 K (at P4 only)
  DFB at 4.5 K with their current leads and superconducting links
  Inner Triplet (IT) at 1.9 K around experiments (dynamic heat loads, depending on luminosity)
  Beam Screens (BS) between 4.5 K and 20 K (dynamic heat loads, depending on beams – sync rad + impedance + ecloud)
Changes for HL-LHC:
The available ARC beam screen cryogenic capacities will slightly increase in HL sectors !
1 Cryoplant capacity
~18 kW @ 4.5 K
~1 kW (5%)
IT heat loads
Basic
Heat loads
~12 kW
(70%)
Beam Screen heat loads
Up to 5 kW
(25%)
Expected changes in HL-LHC | Helium massflow | Q @ 1.9 K [per sector] | BS Capa 4.5 K - 20 K [per ARC] | BS Capa 4.5 K - 20 K [per half-cell of 53m] | Concerned sectors
Removal of IT/D1 at P1 & P5 in LS3 | -12 g/s | -280 W | +1.3 kW | +25 W/hc | S12, S81, S45, S56
No changes expected
for HL-LHC

## Slide 5: Where are we today (2024) ?
LHC Design Report
=85 W/hc
Cryo Beam Screen
capacities for the Run 3
Beam Screen cryogenic heat load averages in each ARC measured during fill #9694
  31st May 2024 with 2352 bunches @ 1.62e11 ppb (3x36b scheme)
Cryogenics is running at its ultimate limit in S78
  BS heat loads are in average more than twice higher than expected
PS: All LHC cryoplants are slightly different and have different capacities & loads (RF, SAM, DFB, triplets, etc.)

## Slide 6: What will happen after LS3 ?
+ 25W/hc
+ 25W/hc
+ 25W/hc
+ 25W/hc
ARC Beam screen capacities will increase in HL sectors by +25 W/hc (IT/D1 removal)
ARC beam screen heat loads will increase due to the HL-LHC beams
(depending on filling schemes and intensities)
+ ???
+ ???
+ ???
+ ???
+ ???
+ ???
+ ???
+ ???
LHC DR
=85 W/hc

## Slide 7: HL-LHC beam screen heat load forecast
E-cloud simulations done by BE-ABP and presented in Chamonix 2023 by Lotta Mether
  Assuming no BS treatment and no more beam screen surface degradation during LS3
  (optimistic scenario)
Fill #9694
(2024 measure in 36bx3)
HL-LHC forecast (48bx5)
 240 W/hc
Additional ARC beam screen heat load expected
with HL-LHC beams
 Does not work !
LHC DR
=85 W/hc
2.3
S23 capacity
=180 W/hc
(no change)

## Slide 8: The same exercise was achieved for each sector











 Impossible to operate HL-LHC with the forecast beams due to the extra heat loads generated by the e-clouds
LHC DR
=85 W/hc

## Slide 9: Proposed solution: Beam Screen Treatment (BST)
Deposit a thin Amorphous Carbon over the BS surface to reduce the e-clouds heat loads (in situ)
Project managed by TE-VSC (G. Rosaz)
Objective is to treat 100 half-cells (2 x 5.3 km) of beam screens during the LS3
Sector margins after treatment if no more degradation: [34,34,52,37,33,35,32,40] W/hc
~15% margin in all sectors is mandatory due to the uncertainly on the treatment efficiency and on potential further BS surface degradations during LS3

## Slide 10: Conclusion
LHC cryogenics infrastructures will remain the same for the ARC cooling in the HL-LHC era
  The cryogenic BS capacities for the ARC will slightly increase after LS3 in the HL sectors
  (~ +10%) due to the removal of the IT+D1 around P1 & P5 from the existing cryoplants
Nevertheless, the HL-LHC beams will induce up to +150% of heat loads on beam screens due to the e-clouds  not manageable by cryo, 5/8 sectors will be above the ultimate limits !
Solutions consists in “treating” 2x5 km of beam screens during LS3 to reduce the e-clouds (carbon coating)
  BST project under study/preparation by TE-VSC, already included in LS3 planning
  This solution would allow to restore enough cryo margin in all ARC for HL-LHC beams
Reducing the e-cloud heat loads handled by the existing LHC cryogenic infrastructures is essential to operate the HL-LHC properly, this is not an option.