Future Circular Collider

INTEGRATION

INTEGRATION MEETING

2024-07-10

| Document identifier: | FCC-INF-MIN-0065 ¦ EDMS 3134736 v.1 |
| --- | --- |
| Date: | 2024-07-10 |
| Work package/unit: | Technical Infrastructures / Integration |

Indico: https://indico.cern.ch/event/1429621/

Participants: Fani Valchkova-Georgieva(chair),

Liam Bromiley (SCE-SAM), Jean-Paul Burnet (ATS-DO), Federico Carra (EN-MME), Halil Deveci (TE-MSC), Klaus Hanke (ATS-DO), Barbara Humann (SY-STI), Damien Lafarge (EN-HE), Giacomo Lavezzi (HSE-RP), Charline Marcel (EN-EL), Dieudonne Ngo'O Ella (EN-ACE), Guillermo Peon (EN-CV), Antonio Perillo Marcone (SY-STI), Audrey Piccini (EN-MME), Roberto Rinaldesi (EN-HE), Ghislain Roy (BE-ABP), Pawel Skupien (EN-HE), Pavlina Trubacova (SY-ABT), Byamba Wicki (SY-EPC), Markus Widorski (HSE-RP),

Agenda

- General Information

- Comments

- Actions

# General Information

In power point document Fani presented the FCC-ee Arc cell cross section (slide 3) with modification on the size of the Raw water (new size DN250) and Reject water (new size DN125).

After request of Byamba Wicki, Fani increased the length of the cable trays in the Arc. In the arc we will have 3 cable trays of 600mm, 2 cable trays of 500mm, 3 cable trays of 400mm, 3 cable trays of 300mm and 3 cable trays of 200mm.

After requests of Timothy Paul Watson, Fani displaced the drain with 200mm clockwise from the centre of the tunnel and change geometry to semi-round. Also, she lowered position of the fresh air duct by 100mm, as that she increased the thickness of the slab to 400mm.

On side 6 Fani presented Experiment cavern cross section with EE Detector which include dimensions of the cavern and detector.

From slide 7 to slide 12 Fani presented cross sections of enlarged machine tunnel sections with total length of 948m from the IP. She showed that we will need of 6 different enlargements which will follow the collider and booster trajectory.

Fani showed the integration study done by Dieudonne Adrien Ngo'O Ella for connection tunnel from Service cavern to Machine tunnel and by-pass tunnel. The proposed size for both tunnels is 5.5m in diameter.

Connection tunnel from service cavern to machine tunnel will house the Cryo (hh machine) service (QRL ø 1100 mm, He recovery line DN 100 mm and Warm recovery line DN 250), CV equipment (2x Chilled water DN300, Compress air DN80, Reject water DN 125 (In), Raw water DN 250 (In), Ventilation ducts in the concrete (In), Drain, He/Smoke Extraction), EL services (6x Cable trays).

By-pass tunnel will house the CV equipment (2x Chilled water DN550, 2x Demineralized water DN550, 2 x Ventilation ducts in the concrete (In/Out), Drain, Smoke Extraction and defuser), EL services (7 x Cable trays, HV cable in the concrete, and Leaky feed) and Robot with rail system.

# Comments

Charline said that Fani has to move the HV cable in the concrete.

Guillermo said that we will have chilled water pipes in the connection tunnels or in the by-pass tunnels.

# Actions

☐ Guillermo and Inigo have to make update scenario of CV systems at point A

☐ Fani has to include chicane tunnel on the side of the orange tunnels (Machine tunnel/Service Cavern connection)

# Next Integration Meeting

The next Integration meeting is foreseen on 14.07.2024.