## Slide 1: SPS Main Power Converters Noise & Regulation Joint Accelerator Performance 2024 Workshop
Charles Genton [SY-EPC-HPC]
10.12.2024

## Slide 2: Content
SPS main power converters overview
SPS mains ripple and compensation measures
Regulation overshoots and possible mitigations
Current glitches and improved diagnostics

## Slide 3: Content
SPS main power converters overview
SPS mains ripple and compensation measures
Regulation overshoots and possible mitigations
Current glitches and improved diagnostics

## Slide 4: SPS main dipoles overview
Ratings: 6 kA / 25 kV, < 20 ppm
12 SMD stations in series + 2 spares
1 common digital current regulator (FGC3)
Analogue voltage regulation and firing in each SMD

## Slide 5: SMD power converter layout
Passive filter
Active filter
Ratings: 6 kA / 2 kV

## Slide 6: SMD regulation structure
x12

## Slide 7: SPS main quadrupoles overview
Ratings: 2.2 kA / 4.0 kV, < 20 ppm
1 SMQ station per circuit (QF/QD) + 1 spare
Digital current and voltage regulators (FGC3)
Analogue firing

## Slide 8: SMQ power converter layout
Ratings: 2.2 kA / 3.6 kV
Passive filter
Passive filter

## Slide 9: SMQ regulation structure

## Slide 10: Content
SPS main power converters overview
SPS mains ripple and compensation measures
Regulation overshoots and possible mitigations
Current glitches and improved diagnostics

## Slide 11
Thyristor Power Converter Noise (Part 1: Theory)
Balanced 50 Hz voltages
DC voltage with large 600 Hz
DC voltage with low 600 Hz
A few 100V…
A few V…

## Slide 12
Thyristor Power Converter Noise (Part 2: Real life)
Unbalanced 50 Hz voltages
Just a few %...
DC voltage with large 600 Hz
+ 50 Hz, 100 Hz, 150 Hz…
DC voltage with low 600 Hz
+ 50 Hz, 100 Hz, 150 Hz…
A few 100V…
Still A few V, but…

## Slide 13
50 Hz
Origin of 50 Hz noise : typically comes from couplings with power circuits
[Hz]
[dB]
[Hz]
[dB]
Converters OFF – QF circuit open
Converters OFF – QF circuit closed
I MEAS QF
0 dB = 1.0 A RMS
There is inherently a 50 Hz current circulating in the magnets because of couplings

## Slide 14
100 Hz
Ideal AC network (balanced phases)
Real AC network (unbalanced phases)
100 Hz noise comes from the rectification of (naturally) unbalanced phases

## Slide 15
How to eliminate theses ripples?
By compensating them!
V LOOP
+ FIRING
V REF
(from I LOOP)
V MEAS
50 Hz Generator
100 Hz Generator
150 Hz Generator
GAIN 50Hz
PHASE 50 Hz
GAIN 100 Hz
PHASE 100 Hz
GAIN 150 Hz
PHASE 150 Hz
HARMONICS COMPENSATION ALGORITHM
V REF*
POWER CONVERTER
FGC Class 63
OP Tools
BSI
DCCT
Compensating BEAM noise VS. Compensating DCCT noise

## Slide 16
Intensity increased by 15-20% for LHC ion beams at injection
Benefits of the compensation - Example
Courtesy of Hannes Bartosik [BE-ABP]

## Slide 17
Confirmation in 2025
Promising results (just before the YETS…)
In 2025 Compensation also available in MBI (See https://indico.cern.ch/event/1447498/)
Questions to answer :
  Is it sufficient to compensate the noise on MBI, QF and QD?
  Effective compensation on the beam still required?
Compensation stable for > 48h !
Courtesy of Hannes Bartosik [BE-ABP]

## Slide 18: Content
SPS main power converters overview
SPS mains ripple and compensation measures
Regulation overshoots and possible mitigations
Current glitches and improved diagnostics

## Slide 19
Auto-tune overshoots – April 2024
Current response to a 170 mA auto-tune step (pink/green)
Response to unfiltered step
Response to filtered step
Issue fixed with 1st order filter on autotune step (red/blue)

## Slide 20
Auto-tune overshoots – September 2024
Current response to a 170 mA filtered auto-tune step
not sufficient anymore with improved beams
Possible solutions:
Use more sophisticated filtering
Retune the current controller
Issue to be addressed during HWC 2025 in close cooperation with OP

## Slide 21: Content
SPS main power converters overview
SPS mains ripple and compensation measures
Regulation overshoots and possible mitigations
Current glitches and improved diagnostics

## Slide 22
Regulation glitches
SFTPRO Flat top
Current Regulation Error
BSI
Current glitch on MBI
Automatic trigger of an oscilloscope not possible with such small perturbations

## Slide 23
Glitch detector
Solution: software glitch detector to collect data for better diagnostic

## Slide 24
Roadmap for 2025
1. Power converters ripple
  Enable harmonics compensation in MBI thanks to SMD13 consolidation
  Make the harmonics compensation properties ppm
2. Regulation overshoots
  Find the best solution with OP mitigate these overshoots
  For re-tuning the current regulators, 5 extra half-days required
3. Regulation glitches
  Understand and fix the glitches thanks to the glitch detector
Some final words:
  Very good cooperation with the SPS team, very interesting challenges to tackle
  Requires a lot of ressources from many persons in EPC!
  What is the priority of these improvements at the scale of CERN projects?
Thank you for your attention!

## Slide 26
Additional measurement in QF

## Slide 27
Oscillations during ramp-up

## Slide 28
Oscillations during ramp-up – 2023 vs. 2024
I ERR 2023
I ERR 2024