## Slide 1: Guidelines for Graphical User Interfaces Operation Panels June 27th, 2011 Johannes Gutleber
R. Gutleber

## Slide 2: Types of GUIs
Supervisory Panels
  For Operations
  WinCC OA
ProShell Procedures
  For machine development (machine physics mode)
  Interactive applications
  C# WPF
Expert applications
  For operations
  Custom applications
Third party
  Existing applications

## Slide 3: Standards and Applied Guidelines
EN 60601-1-1 & -8 apply for medical device parts
  To date not possible to make absolute separation concerning GUIs
  Consequently, norm applies to all operation GUIs
  Norm is implemented via SCADA toolkit (WinCC OA & Navigator)
FAA (Federal Aviation Administration) Human Factors Design Standard 2003, updated. Feb. 24, 2011
NASA Space Shuttle Cockpit design description
US Army TM 5-601, Supervisory Control and Data Acquisition Systems for Command, Control, Communications, Computer, Intelligence, Surveillance and Reconnaissance Facilities, 2006
US Defense Information Systems Color Display Design Guide
Canadian Command Decision Aiding Technology (COMDAT) Operator-Machine Interface (OMI) Style Guide

## Slide 4: Design Principles
Designed for ambient low-light operation
  Neutral background, many screens in control rooms
  Improve readability to reduce eye fatigue
  High contrast to achieve quick and unambiguous identification of exceptional situations
Standardize visual language
  Reduced (max. 7), defined colour coding
  Standardized icon set
Designed for “watch” rather than “continuous interaction”

## Slide 5: Color Scheme

## Slide 6: Color Language
Dark Blue Background
Light blue gray Panel labels
White Nominal data
Light green Panel title and navigation Data fields that can be changed
Red Hi priority alarm, error, failure
Yellow Medium priority alarm
Cyan Low priority alarm or information Missing data
Orange Actual and set data mismatch

## Slide 7: Icons
For important information compliant with EN 60601-1
For applications
  Microsoft Visual Studio 2010 standard icon library
  Made available to developers in SVN

## Slide 8: Alarm Level Categories