## Slide 1: PID/ Instrumentation EESD phase 3
25/07/2024

## Slide 2: Questions
Shall we keep the option or using N2, supplied by a Dewar in the thermal shield cooling circuit, see slide 5.(Issues on helium purity, risk of error)
When sensors (TT1,TT2, TT4) are redundant with CRG CFB setup should we keep them into the cryostat?
How many voltage taps are available at the busbar location? (see with Jerome)
Should we add PCB sensors?
Strain gauges on Tirod for cold mass support: how many wires? Half or full bridge?
Ambiguity numeration of CFB connections on CRNLSQLJ0006, see slides 6. Be sure to use the proper connection for the mechanical integration.

## Slide 3: PID CFB and EESD phase 3
Instrumentation
From CRNLSQLJ0006: https://edms.cern.ch/ui/file/1337211/AF/crnlsqlj0006-v.AF.pdf
Connection 1
Connection 2
Connection 4
Connection 5
Connection 6
Connection 7
Connection 8

## Slide 4: PID EESD phase 3 & Instrumentation list
 | Sensor ID Number | Type of sensor | Name | Nb of cables to extract from cryostat | Redundant sensor in CFB
0 | - |  | Heater | 2 | 
1 | Vtap 1 |  | Voltage Tap Lead A CFB | 0 | 
2 | Vtap 2 |  | Voltage Tap Lead A Nb-Ti splice | 0 | 
3 | Vtap 3 |  | Voltage Tap Lead A MgB2 splice | 1 | 
4 | Vtap 4 |  | Voltage Tap Coil bottom layer jump | 1 | 
5 | Vtap 4 bis |  | Voltage Tap Coil bottom layer jump (redundance) | 1 | 
6 | Vtap 5 |  | Voltage Tap Slice Intercoil top | 1 | 
7 | Vtap 6 |  | Voltage Tap Slice Intercoil bottom | 1 | 
8 | Vtap 7 |  | Voltage Tap Coil top layer jump | 1 | 
9 | Vtap 7 bis |  | Voltage Tap Coil top layer jump (redundance) | 1 | 
10 | Vtap 8 |  | Voltage Tap Lead B MgB2 splice | 1 | 
11 | Vtap 9 |  | Voltage Tap Lead B Nb-Ti splice | 0 | 
12 | Vtap 10 |  | Voltage Tap Lead B CFB | 0 | 
13 | TT1 | PT100 Pipe element | N2 Inlet Temperature | 4 | None
14 | TT2 | PT100 Pipe element | N2 Outlet Temperature | 4 | TT 8321
15 | TT3 | CERNOX Pipe element | GHe Inlet Temperature | 4 | TT 8312
16 | TT4 | CERNOX Pipe element | GHe Outlet Temperature | 4 | TT 8320
17 | TT5 | CERNOX | Coil Former Temperature Bot 1 | 4 | None
18 | TT6 | CERNOX | Coil Former Temperature Bot 2 | 4 | None
19 | TT7 | CERNOX | Coil Former Temperature Bot 3 | 4 | None
20 | TT8 | CERNOX | Splice intercoil | 4 | None
21 | TT9 | CERNOX | Coil Former Temperature Top 1 | 4 | None
22 | TT10 | CERNOX | Coil Former Temperature Top 2 | 4 | None
23 | TT11 | CERNOX | Coil Former Temperature Top 3 | 4 | None
24 | TT12 | PT100 | Thermal Screen Temperature (Evaluate the hotest point of the Themal screen ) | 4 | None
25 | PT1 |  | N2 Inlet Absolute pressure | 2 ? | 
26 | PDT | 0-600 mbar | Inlet/return GHe differential pressure | 2 ? | 
27 | SG1 |  | TiRod Coldmass 1 | 4 | 
28 | SG2 |  | TiRod Coldmass 2 | 4 | 
29 | SG3 |  | TiRod Coldmass 3 | 4 | 
30 | SG4 |  | TiRod Coldmass 4 | 4 | 
31 | SG5 |  | TiRod Coldmass 5 | 4 | 
32 | SG6 |  | TiRod Coldmass 6 | 4 | 
33 | SG7 |  | TiRod Coldmass 7 | 4 | 
34 | SG8 |  | TiRod Coldmass 8 | 4 | 

## Slide 5: PIS EESD phase 3 With option of supplying N2 for thermal shield cooling circuit

## Slide 6: Ambiguity numeration of CFB connections on CRNLSQLJ0006
From CRNLSQLJ0006: https://edms.cern.ch/ui/file/1337211/AF/crnlsqlj0006-v.AF.pdf

## Slide 7: Mechanical integration on CFB vacuum barrier
Connection 2
DN8
20 K GHe
to Cold mass
Connection 5
DN8 70+ K GHe
from Thermal shield
Connection 4 DN8
20+ K GHe
from Cold mass
From CRNLSQLJ0006: https://edms.cern.ch/ui/file/1337211/AF/crnlsqlj0006-v.AF.pdf
From LHCQXCAA0285

## Slide 8: Mechanical integration on CFB vacuum barrier
Connection 2
DN8
20 K GHe
to Cold mass
Connection 5
DN8 70+ K GHe
from Thermal shield
Connection 4 DN8
20+ K GHe
from Cold mass

## Slide 9: Figures

## Slide 10
MgB2/MgB2
Splice inter coil
LN2
from Dewar
to thermal shield
Connection 2 DN8
HP warm GHe + LHe 20K
to Cold mass
Connection 5
DN8 70+ K GHe
from Thermal shield
VTap 9
VTap 2
VTap 8
VTap 3
VTap 4
VTap 5
VTap 6
Coil bottom
Layer bottom
TT 5 COX
TT 6 COX
TT 7 COX
TT 3 COX
TT 4 COX
TT 1 PT100
TT 2
PT100
VTap 10
VTap 1
Nb-Ti/ Nb-Ti
splice
VTap 7
TT 11 COX
TT 10 COX
TT 9 COX
Coil bottom
Layer top
Coil top
Layer top
Coil top
Layer bottom
Cold mass
bottom
Cold mass
top
Thermal shield
TT 12 PT100
Nb-Ti/MgB2
splice & plug
TT 8 COX
PDT 1
Layer jump
Layer jump
Heater
Connection 4 DN8
20+ K GHe
from Cold mass
FT ? ?
TT ? ?
PT ? PT100
GT 8311
GT 8312
FT ??
TT 8312
PT 8312
GT 8327
PDT 8320
TT 8320
PT 8320
GT 8328
PDT 8321
TT 8321
PT 8321
PT 1
Thermal shield
LN2
from thermal shield to exhaust
VTap 4 bis
VTap 7 bis

## Slide 11
MgB2/MgB2
Splice inter coil
Connection 2 DN8
HP warm GHe + LHe 20K
to Cold mass
Connection 5
DN8 70+ K GHe
from Thermal shield
VTap 9
VTap 2
VTap 8
VTap 3
VTap 4
VTap 5
VTap 6
Coil bottom
Layer bottom
TT 5 COX
TT 6 COX
TT 7 COX
TT 3 COX
TT 4 COX
TT 1 PT100
TT 2
PT100
VTap 10
VTap 1
Nb-Ti/ Nb-Ti
splice
VTap 7
TT 11 COX
TT 10 COX
TT 9 COX
Coil bottom
Layer top
Coil top
Layer top
Coil top
Layer bottom
Cold mass
bottom
Cold mass
top
Thermal shield
TT 12 PT100
Nb-Ti/MgB2
splice & plug
TT 8 COX
PDT 1
Layer jump
Layer jump
Heater
Connection 4 DN8
20+ K GHe
from Cold mass
GT 8311
GT 8312
FT ??
TT 8312
PT 8312
GT 8327
PDT 8320
TT 8320
PT 8320
GT 8328
PDT 8321
TT 8321
PT 8321
PT 1
Thermal shield
VTap 4 bis
VTap 7 bis