## Slide 1: An Overview of the Power Converters at CERN
F. Boattini (fulvio.boattini@cern.ch), D. Aguglia (davide.aguglia@cern.ch)
European Organization for Nuclear Research, Accelerator Systems Department, Electrical Power Converter Group
10th September 2024 – FEPPCON 2024

## Slide 2: What are power converters used for at CERN ?
Beams are composed of charged particles (q). These must be guided along the accelerators
Acceleration
Need for HV to create
strong electric fields
Particles pass through an electrical field oriented in the direction of their movement.
Trajectory control
Need for strong magnetic fields:
Electro magnets are used
As the energy of particles
increases the magnetic field controlling
the trajectory must also increase
Power Converters
F. Boattini | Overview of the Power Converters at CERN

## Slide 3
MAGNETS
ELECTRICAL
NETWORK
POWER
QUALITY
RF SYSTEMS
PARTICULE
SOURCE
SEPTA
5300 power converters
from 100 W up to some MW
from 1A up to some kA
from V to some hundred kV
from DC to Cycled or Pulsed mode
from low to high-precision
Spread in the region
On surface and in tunnels
Very different power converter topologies
F. Boattini | Overview of the Power Converters at CERN

## Slide 4: Power converters around the accelerator complex
H- source in LINAC4
HV pulsed low current pulsed
F. Boattini | Overview of the Power Converters at CERN

## Slide 5: Linac4 H- ions source power supply
H- beam to p+
  Linac4 accelerates hydrogen ions;
  At entrance in the PS Booster, the extra e- are stripped away (a more intense p+ beam is obtained)
H- ions source power supply
  H based ions and e- are generated in a plasma source;
  H- (an unwanted e-) are accelerated by a set of HV electric fields (pulsed and DC)
Principle of H- source
Voltage power supplies specification
F. Boattini | Overview of the Power Converters at CERN

## Slide 6: Linac4 H- ions source power supply
One Quadrant linear IGBT regulation
  HV oil insulated pulse transformer generates a trapezoidal voltage pulse;
  The 1% stability on the flattop is achieved by linear regulation of the return IGBT
Topology choice: simple (reliability), no ripple (IGBT in linear mode)
Preload for IGBT linear regulation
Pulse TR magnetic discharge
Voltage oscillations dumping
Arc limiter
Capacitor charger
Controller
Oil Tank
Linearly regulated IGBT
F. Boattini | Overview of the Power Converters at CERN
H- generation

## Slide 7: Power converters around the accelerator complex
Klystron modulator
F. Boattini | Overview of the Power Converters at CERN

## Slide 8: Linac4 RF klystron modulator
Topology: Capacitor discharge, HV pulse transformer, voltage drop correction with bouncer circuit
  Output voltage/current: 110kV / 50A, pulsed at 2Hz
  Voltage drop: 0.5%
  Voltage precision: ±0.5%
  Load pulse length: 1.4ms
  Load: Klystron 2.8MW
RF power amplifier
F. Boattini | Overview of the Power Converters at CERN
8
H- acceleration to PSB

## Slide 9: Linac4 RF klystron modulator
Topology: Capacitor discharge, HV pulse transformer, voltage drop correction with bouncer circuit
  Output voltage/current: 110kV / 50A, pulsed at 2Hz
  Voltage drop: 0.5%
  Voltage precision: ±0.5%
  Load pulse length: 1.4ms
  Load: Klystron 2.8MW
Bouncer correction
F. Boattini | Overview of the Power Converters at CERN
9
Reverse Conducting IGCT

## Slide 10: Power converters around the accelerator complex
PSB and PS “main” power supply
Clean with Energy Storage
F. Boattini | Overview of the Power Converters at CERN

## Slide 11: PS and PSB power supplies
11
PSB and PS beam bending magnets supply
PSB
PS
AC-DC 3phase boost rectifier
DCDC stage to power electromagnets
Energy exchange from Capacitors
F. Boattini | Overview of the Power Converters at CERN

## Slide 12: PS and PSB power supplies
Press-pack technology: 4500V, 2200A
Standard building blocks for 3300V motor applications (marine propulsion, steel makers, LNG compressors etc..)
Three-Level NPC type (3phase) brick.
3300V motor drive re-arranged with interleaving
F. Boattini | Overview of the Power Converters at CERN
IEGT 4.5kV 2200A PP IGBT

## Slide 13: Power converters around the accelerator complex
SPS “mains”
Classical thyristor rectifier
Reactive power compensation is required
F. Boattini | Overview of the Power Converters at CERN

## Slide 14
SPS beam bending magnets supply
Power: 6 kA / 25 kV, < 20 ppm
12 SMD stations in series + 2 spares
Standard 12 pulse rectifiers
SPS “mains” power converter
[s]
[A] / [V]
5.8 kA
25 kV
Phase control PP thyristor

## Slide 15: SPS “mains” Static Var Compensators
Thyristor rectifiers:
AC current is shifted by  (fundamental)
AC side active and reactive power (neglecting harmonics):
P=3*Vphase*Iline*cos()
Q=3*Vphase*Iline*sin()
Huge reactive power at low DC voltages…
[s]
[A] / [V]
SVC
~150MW/Mvar in about 15s
Solution
15

## Slide 16
Harmonic Filters: 130 Mvar
Thyristor Controlled Reactor: 150 Mvar
SVC: Static Var Compensator for the SPS
  Harmonic filtering
  Network voltage stabilization
F. Boattini | Overview of the Power Converters at CERN
Phase control PP thyristor

## Slide 17: Power converters around the accelerator complex
Superconducting magnets in the LHC
F. Boattini | Overview of the Power Converters at CERN

## Slide 18: Power converters for superconducting magnets in the LHC
LHC beams bending / focusing magnets supply
High currents up to 13kA and low voltages up to 180V
  Three quadrupole magnets focus the beams down to 16um before collision
  Example: Inner triplet
  Provides proton beams final focusing before Interaction Points (IP)
  Powering with independent regulation:
  2kA 8V basic block
F. Boattini | Overview of the Power Converters at CERN

## Slide 19: Power converters for superconducting magnets in the LHC
  One quadrant soft switching power converter
  Output Module
F. Boattini | Overview of the Power Converters at CERN
  1.2kV, 150A IGBT module
  Input Module
  Basic power block: 2kA, 8V

## Slide 20: The biggest challenge?
All 5300 Power Converters, the control, the cooling, the vacuum …. Humans…
They all must work together, reliably and at the same time!
Thanks for your time
At CERN we do it!
F. Boattini | Overview of the Power Converters at CERN

## Slide 22: Power converters around the accelerator complex
Transfer lines, Experimental areas etc..
Power converters with energy storage
F. Boattini | Overview of the Power Converters at CERN

## Slide 23: SIRIUS: Energy recovery in transfer lines
IGBT legs
IGBT drivers
Interface card
DC-link capacitors
Energy Recovery with Elco capacitors
SIRIUS 4P+
SIRIUS 4P
Large dipoles & series-connected magnets
Extra large dipoles & high energy beams
SIRIUS 2P
SIRIUS S
Small quadrupoles & correctors
Small quadrupoles & dipoles
150 power converters across all the families
F. Boattini | Overview of the Power Converters at CERN
Transfer to other accelerators or experiments
IGBT module